## Sheet1
TDSP | Major Transmission Element (MTE) | Equip. Type | kV | Congestion Year/Month | Contingency | Overload | Source | Outage Type | Cancel | Removal Requestor | Reason for Removal | OCITF Consensus | Decision | Discussion Items | From Acronym | To Acronym | ERCOT Equip Name | ERCOT Contingency ID
AEP, CNP | South Texas Project - Whitepoint | LN | 345 | 17/9, 17/11, 17/12, 18/1, 18/3 | Lon Hill to Coleto Creek 345 kV, DCKT San Miguel Gen to Elmcreek 345 kV, DCKT Haisley to Warburton Road Switching Station 138 kV & Lon Hill to Coleto Creek 345 kV, San Miguel Auto 345_138 kV Switchyards Trx SANMGL8_3_1 345/138 kV, Dyann to Wharton 138 kV, Danevang Switching Station to Blessing 138 kV | Lon Hill - Pawnee Switching Station 345 kV, Pawnee Switching Station - Calaveras 345 kV, Blessing Auto 69A1 138/69 kV, El_Campo - Lane City Pump 138 kV | RT | Forced | [6 empty] | WHITE_PT | STP | STPZWP39 | SWHISTP5
CNP | Alta Loma - Ph Robinson | LN | 138 | 18/5 | DCKT Sr Bertron - Dowlap & Quanab 138 kV | Angleton - Liverpool 138 kV | RT | Forced |  | CNP | Congestion caused by multiple forced outages related to the failure of PHR A4. Reconfiguration and replacement projects have since been completed to relieve this congestion. TPIT: 6312B & 43531 |  |  |  | PHR | AL | AL_PHR93 | SALPHR8
CNP | Baytown - … - Haney | LN | 138 | 18/5 | DCKT Cedar Bayou Plant - Quanum & Strang 138 kV | Diamond Battleground - Moment 138 kV | RT | Planned |  | CNP | Congestion caused by multiple forced outages related to the failure of PHR A4. Reconfiguration and replacement projects have since been completed to relieve this congestion. TPIT: 6312B & 43531 |  |  |  | BT | HL | BT_HL_66 | SHNYBT8
CNP | Bellaire - … - Britmoore | LN | 138 | 19/4 | Meadow - PH Robinson 345 kV | Alvin Tnp - Mainland Tnp 138 kV | RT | Planned |  | CNP | The cause of congestion is unlikely and we are unable to recreate. The outage in question is a 138kV line on the west side of our system, and is one of many parallel paths between major substations. A 345kV contignency on the East side of our system should not cause congestion on our Eastern 138kV ties when paired with this outage. |  |  |  | BI | BM | BI_UL_24 | SULBI8
CNP | Bellaire - Wa Parish | LN | 345 | 16/10 | DCKT Wa Parish to Jeanetta 345 kV | Bellaire - Smithers 345 kV | ST | Planned | [6 empty] | BI | WAP | BI_WAP50 | SBIWAP5
CNP | Blessing - South Texas Project | LN | 345 | 18/12 | DCKT Wa Parish - Bailey & Hillje 345 kV | Jones Creek - South Texas Project 345 kV | RT | Planned, Forced | [6 empty] | STP | BLESSING | BLESSING | SBLESTP5
CNP | Bunker - H O Clarke | LN | 138 | 18/11 | Meadow - North Alvin Tap 138 kV | Grant - Teco 138 kV | RT | Planned |  | CNP | Project to increase rating of line 37 Teco to Grant Completed TPIT: 5767 |  |  |  | BUN | HOC | BUNHOC08 | SBUNHO28
CNP | Camden - Surfsi | LN | 138 | 18/12 | DCKT Wa Parish - Bailey & Hillje 345 kV | Dow Chemical - South Texas Project 345 kV | RT | Planned, Forced |  | CNP | Line does not exist. |  |  |  | SRF | VL | SRFVL_59 | SSRFV2L8
CNP | Chambers - King | LN | 345 | 17/9, 17/10, 18/3 | Meadow to Oasis 345 kV, Ph Robinson to Center 345 kV, DCKT Crown to Tanker & Davson to Greens Bayou 138 KV | Angleton - Liverpool 138 kV, Channelview - Lynch 138 kV, Exxon - Lynch 138 kV, Bigvue - Power Systems - Arco Cogen 138 kV | RT | Planned, Forced |  | CNP | Congestion caused by multiple forced outages related to the events of Harvey. Multiple 345kV lines were taken out to repair errosion, which coincided with multiple planned 138kV outages to create congestion. |  |  |  | CHB | KG | CHBKG_97 | SCHBKG5
CNP | Crosby - Power Systems Arco Cogen | LN | 138 | 19/3 | DCKT Chambers - King & Jordan - North Belt 345 kV | Bigvue - Power Systems Arco Cogen 138 kV | RT | Planned, Forced | [6 empty] | CS | HNY | CS_HL_08 | SHLC6S8
CNP | Derick - South Channel | LN | 138 | 18/5 | DCKT Cedar Bayou Plant - Quanum & Strang 138 kV, DCKT Sr Bertron - Dowlap & Quanab | Diamond Battleground - Moment 138 kV, Angleton - Liverpool 138 kV | RT | Planned |  | CNP | Congestion caused by multiple forced outages related to the failure of PHR A4. Reconfiguration and replacement projects have since been completed to relieve this congestion. TPIT: 6312B & 43531 |  |  |  | DER | SC | DERSC_85 | SDERSC8
CNP | Dow Chemical - South Texas Project | LN | 345 | 18/12, 19/1, 19/3 | DCKT Wa Parish - Bailey & Hillje 345 kV | Jones Creek - South Texas Project 345 kV | RT | Planned | [6 empty] | STP | DOW | DOWSTP27 | SSTPDOW5
CNP | Freeport - Surfsi | LN | 138 | 18/12 | DCKT Wa Parish - Bailey & Hillje 345 kV | Dow Chemical - South Texas Project 345 kV | RT | Planned, Forced | [6 empty] | FP | SRF | FP_SRF59 | SFPSRF8
CNP | Garrott - Kirby (GT_KB_37) | LN | 138 | 17/9 | Meadow to Oasis 345 kV | Angleton - Liverpool 138 kV | RT | Planned |  | CNP | Congestion caused by multiple forced outages related to the events of Harvey. Multiple 345kV lines were taken out to repair errosion, which coincided with multiple planned 138kV outages to create congestion. |  |  |  | GT | KB | GT_KB_37 | SGTKB8
CNP | Greens Bayou - … - Lychem | LN | 138 | 18/5 | DCKT Cedar Bayou Plant - Quanum & Strang 138 kV | Diamond Battleground - Moment 138 kV | RT | Planned, Forced |  | CNP | Congestion caused by multiple forced outages related to the failure of PHR A4. Reconfiguration and replacement projects have since been completed to relieve this congestion. TPIT: 6312B & 43531 |  |  |  | UV | GBY | GBYUV_08 | SLHMGB28
CNP | Greens Bayou Auto AT2 | XF | 345 | 16/2 | DCKT Greens Bayou to King 345 kV | Greens Bayou Auto AT1 345/138 kV | ST | Planned | [6 empty] | GBY |  | AT2 | XGB2Y58
CNP | H O Clarke - … - Southwyck | LN | 138 | 18/3 | DCKT Crown to Tanker & Davson to Greens Bayou 138 KV | Bigvue - Power Systems - Arco Cogen 138 kV | RT | Planned |  | CNP | HOC-SO 05 has been reconfigured and is currently a radial and the congestion has not occurred since. |  |  |  | HOC | IR | HOCIR_05 | SIRSO8
CNP | Hillje - Wa Parish (HLJWAP64) | LN | 345 | 16/3 | DCKT South Texas Project to Dow Chemial & Jones Creek 345 kV | South Texas Project - Wa Parish 345 kV | RT | Planned | [6 empty] | HLJ | WAP | HLJWAP64 | SHLJWA25
CNP | Jewett - Limestone (225) | LN | 345 | 15/3 | DCKT Limestone to Twin Oak Sw 345 kV | Big Brown Ses - Jewet (50) | ST | Planned |  | CNP | Houston Import Project system upgrades completed in 2018 allievates congenstion. TPIT: 3937 |  |  |  | JEWET | LEG | 225 | SLEGJE35
CNP | Jones Creek - South Texas Project | LN | 345 | 18/12, 19/1, 19/4 | DCKT Wa Parish - Bailey & Hillje 345 kV, DCKT Hillje - Wa Parish & Bailey 345 kV | Dow Chemical - South Texas Project 345 kV | RT | Planned | [6 empty] | JCK | STP | JCKSTP18 | SJCKSTP5
CNP | Jordan - North Belt | LN | 345 | 17/9, 17/10 | Meadow to Oasis 345 kV, Ph Robinson to Center 345 kV | Angleton - Liverpool 138 kV, Channelview - Lynch 138 kV, Exxon - Lynch 138 kV | RT | Forced |  | CNP | Congestion caused by multiple forced outages related to the events of Harvey. Multiple 345kV lines were taken out to repair errosion, which coincided with multiple planned 138kV outages to create congestion. |  |  |  | JOR | NB | JORNB_99 | SCBYNB5
CNP | New Gulf - South Lane City | LN | 138 | 15/12 | DCKT Wharton to East Bernard & Dyann 138 kV (UNSOLVED) | N/A | ST | Planned |  | CNP | Has not occurred again. No issues with internal case solving |  |  |  | LC | NEW | LC_NEW60 | STGFLC8
CNP | Ph Robinson - Webster | LN | 138 | 18/5 | DCKT Sr Bertron - Dowlap & Quanab 138 kV | Angleton - Liverpool 138 kV | RT | Forced |  | CNP | Congestion caused by multiple forced outages related to the failure of PHR A4. Reconfiguration and replacement projects have since been completed to relieve this congestion. TPIT: 6312B & 43531 |  |  |  | PHR | WEB | PHRWEB93 | SWEBPHR8
CNP | White Oak Auto AT3 345/138 kV | XF | 345 | 16/6 | DCKT Britmoore to Sauer 138 kV | Bellaire - San Felipe 138 kV | RT | Planned |  | CNP | Project to increase rating of line 09 Bellaire to San Felipe Completed TPIT:4703A |  |  |  | WO |  | AT3H | XW2O58
CNP, CPS | Elm Creek - South Texas Project (STPELM18) | LN | 345 | 16/4 | DCKT Marion to Clear Springs & Zorn 345 kV | Comal - Henne 138 kV | ST | Planned | [6 empty] | STP | ELMCREEK | STPELM18 | SELMST25
CNP, CPS | Elm Creek - South Texas Project (STPELM27) | LN | 345 | 16/4 | DCKT Marion to Clear Springs & Zorn 345 kV | Comal - Henne 138 kV | ST | Planned | [6 empty] | STP | ELMCREEK | STPELM27 | SELMSTP5
CNP, TNMP | Gaf Tnp - Ph Robinson | LN | 138 | 18/1 | Caddo Sw Sta Tnp to Greenbelt Tnp 138 kV | Tejas Tnp - Comanche Sw Tnp 138 kV | RT | Planned | [6 empty] | PHR | GAF | GAF_PHR | SGAFPHR8
CNP, TNMP | Hidden Lakes Tnp - PH Robinson | LN | 138 | 18/12 | Lane City - South Lane City 138 kV | Franklins Camp Sub - Sargent Sub 69 kV | RT | Planned, Forced |  | CNP | Congestion was likely due to other outages. The outage, contingency, and overload are ties to separate islands. It is unlikely the three are related. |  |  |  | HDNLAKES | PHR | G138_8A | SPHRHDN8