## Slide 1
Panhandle Stability Study Update
Jeff Billo
Transmission Planning
ERCOT ROS Meeting
August 8, 2019

## Slide 2: Outline
Recap of Previous ROS Update
Panhandle Stability – Existing Condition
Panhandle Stability – With LP&L Integration
Next Steps

## Slide 3: 1. Recap of Previous ROS Update
Increasing nearby Panhandle WGRs help the system response to disturbances at lower system strength levels (similar to the 2018 study findings)
Angular instability (new constraint)
Voltage instability (new constraint)
Next steps:
  Further studies for the existing condition (normal and planned outages; tentative schedule: June/July, 2019)
  Work with TSPs to investigate the feasibility of damping support from synchronous condensers and dynamic reactive devices in the Panhandle to improve the angular stability

## Slide 4: 1. Recap – Panhandle Stability and Assessment Tools
Planning Tools
PSCAD
Operation Tools
WSCR
Offline Tables
Stability Issues
Control System Stability
Angular Stability
WSCR
PSS/E Dynamics
Voltage Stability
VSAT
VSAT

## Slide 5: 2. Panhandle Study– Existing Condition
Panhandle
Nearby Panhandle
*the boundary is only for illustration purpose
Study Scenario | Panhandle WGR Capacity (MW) | Nearby Panhandle WGR Capacity (MW)
Existing/Operational | 3988 | 2219

## Slide 6: 2. Panhandle Stability – Existing Condition
Consider normal conditions and the following eight double circuit outage conditions:
  Riley – Tesla/Jim Treece
  Edith Clarke – Tesla
  Cottonwood – White River
  Cottonwood – Dermott
  Clear Crossing – Edith Clarke/Smoky Hill
  Riley – Edith Clarke
  Tule Canyon – Tesla
  Gray – Tesla
Dynamic stability analysis (PSS/E) was run for all normal and outage conditions to identify the stability limits
WSCR and VSAT analyses were also conducted to evaluate the existing WSCR and VSAT criteria

## Slide 7: 2. Findings – Existing Condition
Studied level of wind generation nearby Panhandle improves performance with respect to system strength
Voltage collapse observed in PSS/E at higher steady state voltage levels, especially under outage conditions
Under normal and most outage conditions, WSCR of 1.5 and VSAT with revised voltage criteria at 0.93 pu are adequate
Under specific outage conditions, neither WSCR of 1.5 nor VSAT can properly identify the dynamic voltage stability limit
Panhandle WGRs
Nearby
Panhandle WGRs
3988 MW
SCs
ERCOT Grid
2219MW

## Slide 8: 2. Conclusion – Existing Condition
The existing interface and WSCR of 1.5 are adequate
VSAT criterion has been revised in real-time tool to properly determine the stability limit under most outage conditions
Off-line stability limit under specific outage conditions is being implemented
Panhandle WGRs
Nearby
Panhandle WGRs
3988 MW
SCs
ERCOT Grid
2219MW

## Slide 9: 3. Panhandle Stability – with LP&L Integration
Consider normal conditions, the following eight double circuit outage conditions and two single circuit outage conditions:
  Riley – Tesla/Jim Treece
  Edith Clarke – Tesla
  Cottonwood – White River
  Cottonwood – Dermott
  Clear Crossing – Edith Clarke/Smoky Hill
  Riley – Edith Clarke
  Tule Canyon – Tesla
  Gray – Tesla
  Ogallala – Abernathy (P1)
  Long Draw – Grassland (P1)
Dynamic stability analysis (PSS/E) was run for all normal and outage conditions to identify the stability limits
WSCR and VSAT analyses were also conducted to evaluate the existing WSCR and VSAT criteria

## Slide 10: 3. Panhandle Stability – with LP&L Integration
The LP&L integration provides an additional transfer path between the Panhandle and the rest of the ERCOT grid
Several WGRs’ dynamic models (PSS/E and PSCAD, provided by REs) didn’t include the power plant controllers (PPC), as a result, those WGRs were set to regulate the terminal voltage instead of high side of transformer or POI
Panhandle WGRs
Nearby
Panhandle WGRs
5182 MW
SCs
ERCOT Grid
3174MW
LP&L Integration

## Slide 11: 3. Findings – with LP&L Integration
The proposed WSCR calculation method is based on the assumption of full interactions between wind plants. This is equivalent to assuming all wind plants are connected to a single virtual Point of Interconnection (POI)
  The additional export path, nearby LP&L load, and increasing nearby Panhandle generation make WSCR a less appropriate metric to identify the Panhandle stability limit
Although improved system response with LP&L integration is expected, unacceptable results (small signal instability) for 100% Panhandle dispatch were observed – this may be due to model performance issues (see May ROS Update)
  The PSS/E limit was 5052 MW under normal (no outage) conditions
    Limit not yet verified in PSCAD

## Slide 12: 3. Sensitivity Analysis – with LP&L Integration
ERCOT performed a sensitivity analysis in PSS/E by adding a PPC model for those WGRs that did not have PPC representation and setting all WGRs to regulate the voltage at high side of transformer or POI
Under normal conditions (no outage), acceptable responses were obtained at 100% Panhandle and Nearby Panhandle dispatch
  i.e. stability limit is higher than 5182 MW Panhandle + 3174 MW Nearby Panhandle generation
  Not yet verified in PSCAD
Under outage conditions, voltage stability and small signal instability are the most limiting constraints
  VSAT with revised criterion can properly determine the stability limit under most outage conditions, though this may be conservative in some cases
  Off-line stability limit under specific outage conditions may need to be considered

## Slide 13: 4. Next Steps
Work with REs/developers to confirm the voltage regulation settings and resolve potential model performance issues - updated models may need to be submitted (target Q4, 2019)
Continue to evaluate the proper approach to manage the stability constraints in operations under various outage conditions
Work with TSPs to investigate the feasibility of damping support from synchronous condensers and dynamic reactive devices in Panhandle to improve the angular stability
Study evolving conditions between now and expected LP&L integration

## Slide 14
Questions?