## Slide 1
ERCOT Frequency Control Report
July 2019
ERCOT
Operations Planning
PDCWG | August 14th, 2019

## Slide 2: Summary of July 2019
CPS1: 176.97%
Current CPS1 12-Month Rolling Average: 176.97%
3 BAAL Exceedances
3 hourly CPS1 scores below 100%
BAAL-003 Events have updated through 2018
2018 BAAL-003 FRM Performance: -843.17
2019 RMS1 Statistics
  Mean: 14.36 mHz
  Min: 11.81 mHz
  Max: 16.96 mHz
Energy Statistics
  Total Energy: 39,226,761 MWh
  Wind Energy: 6,150,047 MWh
  Percent Energy from Wind: 15.68%
  Solar Energy: 464,456
  Percent Energy from Solar: 1.18%
Minimum System Inertia
  Mean: 275,707
  Max: 324,355 on Jul 11th
  Min: 242,244 on Jul 27th

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
Jul-19 CPS1 (%): 176.97
Notes: Outliers:
7/12/2019 17:00 89.1%
Large expected generation deviation from conventional and IRRs for most of the hour.
7/16/2019 12:00 83.5%
Several units above their BPs due to changing configurations or in startup at top and end of hour. Also Unit runback/trip in middle of hour.
7/29/2019 18:00 78.5%
Large expected generation deviation from conventional and IRRs for most of the hour.

## Slide 5: BAAL Exceedances & Violations
There were 3 BAAL exceedances in July
  July 29, 2019
    Unit Trip at 17:59:12
    Loss of 817 MW
    Less than 59.91 Hz for 3 minutes

## Slide 6: 15-Minute Average CPS1%
Jul-19 CPS1 (%): 176.97

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 174.33%

## Slide 8: Daily RMS1 of ERCOT Frequency by Year
Notes: Mean is 15.07 mHz

## Slide 9: Daily RMS1 of ERCOT Frequency by Month

## Slide 10: Daily RMS1 of ERCOT Frequency by Month
Notes: Mean: 14.36 mHz
Min: 11.81 mHz
Max: 16.96 mHz

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison

## Slide 13: Frequency Profile Comparison

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2018 BAL-003 Selected Events – Update
Notes: BAL-003

## Slide 19: Op. Year 2018 BAL-003 FRM Performance - Update

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 39,226,761 MWh

## Slide 22: Total Energy from Wind Generation
Notes: 6,150,047 MWh

## Slide 23: % Energy from Wind Generation
Notes: 15.68%

## Slide 24: Total Energy From Solar Generation
Notes: 464,456 MWh

## Slide 25: % Energy from Solar Generation
Notes: 1.18%

## Slide 26: ERCOT System Inertia

## Slide 27: Daily Minimum System Inertia
Notes: Minimum Inertia = 128,759 MW*s on 11/3/2018.
Previous Minimum was 130,014 MW*s on 10/27/2017. This was also our record wind day.
Data:
Mean: 275,707
Max: 324,355 on Jul 11th
Min: 242,244 on Jul 27th

## Slide 28: Questions?
Thank you!