## Slide 1
Southern Cross Transmission Directives
Directive #3 : Ramp rate
August 2019, PDCWG
ERCOT Staff

## Slide 2: Directive #3
ERCOT shall determine what ramp rate restrictions, if any, will be necessary to accommodate the interconnection of the Southern Cross DC tie and shall implement those restrictions and shall certify to the Commission when it has completed these actions.
Upon the interconnection of Southern Cross Transmission DC Tie, there is a potential of up to a 4100 MW change in the DC tie’s schedule (based on the projected maximum import/export capability of the tie).
In order to determine whether ramp rate restrictions should be imposed on the DC tie, ERCOT and PDCWG evaluated;
  the impact to ERCOT’s net load variability due to a DC tie ramp of this magnitude, and
  the impact on ERCOT’s ability to recover from frequency events such as Reportable Balancing Contingency Events during the DC Tie ramps.
  Existing process for managing DC Tie schedules

## Slide 3: Recap of Directive #3 Discussions at PDCWG
ERCOT introduced Southern Cross Directive #3 at the April, 2019 PDCWG meeting. http://www.ercot.com/content/wcm/key_documents_lists/166244/Directive_3_Discussion_Points_v3.docx
  At the April 2019 PDCWG meeting, stakeholders requested ERCOT to provide high level overview of how the DC Ties are managed by Control Room today.
  Stakeholders also requested additional data related to usage of regulation during the DC tie ramps as well as historical net load ramp data.
At the June, 2019 PDCWG Meeting ERCOT presented both the items requested by the stakeholders.
  http://www.ercot.com/content/wcm/key_documents_lists/166255/ERCOT_DC_Tie_Procedure.pptx

## Slide 4: Managing DC Tie Schedules
ERCOT is responsible for approving/rejecting the E-Tags that are submitted to ensure ERCOT BA can support requested flows (NERC Standard INT-006-4 R1).
ERCOT Control Room has procedures (DC Tie Operating Procedure, ERCOT DC Tie Operations) to monitor, approve and/or curtail DC Tie schedules.
  Per this procedure ERCOT analyzes the ramping capability available to support DC Tie Schedules
  DC Tie ramps typically 10 mins long and occur at the top of the hour. In case of reliability concerns ERCOT has the ability to extend the duration of the ramp or de-rate the associated DC Tie.

## Slide 5: SCR 800 Addition of DC Tie Ramp to GTBD Calculation
ERCOT’s Generation To Be Dispatched (GTBD) calculation does not currently account for DC Tie ramp schedules. DC Tie imports or exports may cause delay in the recovery of system frequency following a Frequency Measurable Event (FME)
  SCR 800 Addition of DC Tie Ramp to GTBD Calculation has been submitted to incorporate DC Tie schedules into GTBD.
    Add a K7 configurable factor together with the DC Tie Ramp Rate (DCTRR) calculated in the Energy Management System (EMS) using approved DC Tie Electronic Tags (e-Tags).
The GTBD equation should be as follows:
Generation To Be Dispatched = Total Gen + K1*10*System Load Frequency Bias + K2*[(net non-conforming Load) – (net filtered non-conforming Load)] + K3*5*PLDRR + K4*Regulation Deployed + K5*ACE Integral – K6*5*PWRR + K7*5*DCTRR
DCTRR = DC Tie Ramp Rate where a positive value indicates increasing export and a negative value indicates increasing import

## Slide 6: Proposed Next steps
DC Tie Schedules management process;
  Today DC Tie schedules can be submitted as late as 20 minutes prior to scheduled ramp
  What should be the minimum lead time for submitting DC Tie Schedules for Southern Cross DC Tie?
  RUC today does not take ramping capability needed to support DC tie schedules into account.
Does existing framework in place (including NPRR 825) need to be modified to put ramp limitation on Southern Cross DC Tie?
SCR 800 upon approval will incorporate DC Tie schedules and help Security-Constrained Economic Dispatch (SCED) better issue Base Points to Generation Resources to account for the ramping of DC Ties in the next 5 minutes.
Should the Southern Cross DC Tie will be required to implement a UDBP freeze logic similar to Generation Resources (see below)?
6.5.7.6.1 LFC Process Description
(9) If system frequency deviation is greater than an established threshold, ERCOT may issue Dispatch Instructions to those Resources not providing Reg-Up or Reg-Down that have Base Points directionally opposite ACE, to temporarily suspend ramping to their Base Point until frequency deviation returns to zero.

## Slide 7
Questions?