## Audit Checklist
EPS Site Audit Form Version 6.1 - 1/1/2020
Site: |  |  | Design Proposal Approval Date: |  |  |  | Auditor:
Meter Point: |  |  | Project #: |  |  |  | Audit Date:
| Specific Item Check | Protocol Reference | Resource | Check Method | How Confirmed | Requirement Meet | Comment
Design Proposal/Facility Details Information
New # | Facility Details
1.1.1 | Does One Line accurately reflect the EPS Metering configuration including breakers/by-passes that would affect the metered energy flow? | Protocol 10.4.2(1), SMOG Section 3.2.1(1)(b), 3.2.1(1)(c ) and 3.2.3(1)(h)
1.1.2 | Do breakers exist where one line diagram indicates? | Protocol 10.4.2(1), SMOG Section 3.2.1(1)(b), 3.2.1(1)(c ) and 3.2.3(1)(h)
1.1.3 | Are CT's located as one line diagram indicates? | Protocol 10.4.2(1), SMOG Section 3.2.1(1)(b), 3.2.1(1)(c ) and 3.2.3(1)(h)
1.1.4 | Are VT's located as one line diagram indicates? | Protocol 10.4.2(1), SMOG Section 3.2.1(1)(b), 3.2.1(1)(c ) and 3.2.3(1)(h)
1.1.5 | Do three lines and one line drawings match one another? | Protocol 10.4.2(1), SMOG Section 3.2.1(1)(b), 3.2.1(1)(c ) and 3.2.3(1)(h)
1.1.6 | CT Ratio-Does design approved ratio match existing CT ratio? If dual ratio, is the connected ratio correct? | Protocol 10.4.2(1), SMOG Section 3.2.1(1)(b), 3.2.1(1)(c ) and 3.2.3(1)(h)
1.1.7 | PT Ratio-Does design approval ratio match existing VT ratio? If dual ratio, is the ratio connected correct? | Protocol 10.4.2(1), SMOG Section 3.2.1(1)(b), 3.2.1(1)(c ) and 3.2.3(1)(h)
1.1.8 | VT Polarity-Are polarity's oriented the correct direction with reference to the design proposal? | Protocol 10.4.2(1), SMOG Section 3.2.1(1)(b), 3.2.1(1)(c ) and 3.2.3(1)(h)
1.1.9 | CT Polarity-Are polarity's oriented the correct direction with reference to the design proposal? | Protocol 10.4.2(1), SMOG Section 3.2.1(1)(b), 3.2.1(1)(c ) and 3.2.3(1)(h)
ERCOT Point of Interconnection
1.2.1 | Netting Scheme-Does physical distance of 400 yards meet protocol? | Protocol 10.3.2.3
1.2.2 | Are EPS meters connected to the ERCOT grid as shown on the Approved Design Proposal? | Protocol 10.3.2.2
1.2.3 | Are EPS meters compensated once and only once if needed? | Protocol 10.3.2.2
Physical Facility Compliance
Facility
2.1.1 | Does facility environment provide acceptable operating conditions for metering equipment? | SMOG Section 1.5.1(1)
2.1.2 | Does facility meet the requirement outlined in the NESC, Article 125a? | SMOG Section 1.5.1(2)
2.1.3 | Enclosures-Does EPS metering reside in protected enclosure or structure? | SMOG Section 1.5.2(1)(a)
2.1.4 | Test Switch Location-Are test switches located at or near the EPS meters? | SMOG Section 1.5.2
2.1.5 | Test Switch Functionality-Are test switches wired to allow for removal of a meter without affecting other EPS meters? | SMOG Section 1.5.2(1)(c)
2.1.6 | Current Shorting Relay Test Block-Is current circuit wired so that during testing there is no disruption to other meters? | SMOG Section 1.5.2(1)(d)
2.1.7 | Lighting-Does facility provide adequate lighting? | SMOG Section 1.5.2(1)(b)
2.1.8 | Test Output-Is the electrical test output conveniently accessed? | SMOG Section 1.5.2
2.1.9 | Are metering facilitates and secondary devices sealed to protect against unauthorized entry? | Protocol 10.10.1.5
2.1.10 | Are existing seals approved ERCOT seals? | Protocol 10.10.1.5
2.1.11 | Do existing seals match most recent submitted test report? | Protocol 10.10.1.5
Meter Accuracy Test & Load Check Verification
MDAS Form (Channel Information)
3.1.1 | Channel Assignments-Do IDR programmed channels match the submitted MDAS form? | SMOG Section 4.1
3.1.2 | Dials-Do number of energy digits match the submitted MDAS form? | SMOG Section 3.2.2(1)(a)
3.1.3 | UOM-Do device Unit of Measure codes match the submitted MDAS form? | SMOG Section 3.2.2(1)(a)
3.1.4 | Meter Serial Number, Type & Phone number-Does device serial number, model type and phone number match the submitted MDAS form? | SMOG Section 3.2.2(1)(a)
3.1.5 | Do UOM's, Register ID's & Direction of Flow confirm with MDAS staff? | SMOG Section 3.2.2(1)(a)
Multipliers
3.2.1 | Do pulse constants verify the IDR pulse multiplier values on the MDAS and pulse calculation sheet? | SMOG Section 3.3.2
3.2.2 | Based on Design Proposal peak load values, does programmed pulse value prevent pulse overflow? | SMOG Section 3.3.2
3.2.3 | Do present load conditions satisfy the nominal calculated pulse values with reference to the approved design proposal and load calculations? | SMOG Section 4.6
3.2.4 | Does the IDR generate 25% of maximum pulses for nominal load conditions? | SMOG Section 4.6
3.2.5 | Do programmed register constants match the Meter Multiplier calculation sheet? | SMOG Section 3.3.1
3.2.6 | Based on Design Proposal peak load values, does programmed register constant prevent register rollover? | SMOG Section 3.3.1
3.2.7 | Do register multiplier values agree with calculation formula? | SMOG Section 3.3.1
Meter Program Parameters
3.3.1 | Are EPS meters internal energy registers mapped to the proper IDR channels? | SMOG Section 4.1
3.3.2 | Measured Quantities-Are EPS meters programmed for four quadrant measurement? | SMOG Section 6.3.1
3.3.3 | Event Logging-Does EPS meter have all required events enabled? | SMOG Section 6.5.4
3.3.4 | Diagnostic Checks-Does EPS meter have required diagnostics enabled? | SMOG Section 6.5.1, 6.5.2
Calibration Standard
3.4.1 | Test Equipment-Are watthour and varhour standards equal to or better than the accuracy of EPS meters? | SMOG Section 1.6.1
3.4.2 | Standard Certification-Have watthour and varhour standards been tested within the last 120 days? | SMOG Section 1.6.2
3.4.3 | Correction Factors-Do correction factors exist for test standards and are they retained with standards? | SMOG Section 1.6.2
Testing Records
3.5.1 | Are proper test amps and power factors applied for KWH test? | SMOG Section 1.6.5
3.5.2 | Are KWH functions within allotted accuracy tolerance? | SMOG Section 1.6.5
3.5.3 | Are proper test amps and power factors applied for KVARH test? | SMOG Section 1.6.5
3.5.4 | Are KVARH functions within allotted accuracy tolerance? | SMOG Section 1.6.5
3.5.5 | Test Records- Are test records available for last six years? | SMOG Section 1.7.2(1)
3.5.6 | Test Data-Is test data recorded on approved ERCOT Meter Test Report? | SMOG Section 1.8(1)(c)
Loss Calculation Verification
Transformer Loss Values
4.1.1 | Does information entered on Loss calculation sheet match the site facility data? | SMOG Section 8
4.1.2 | High Voltage Rating-Does voltage rating match manufacturer sheet? | SMOG Section 8
4.1.3 | Low Voltage Rating-Does voltage rating match manufacturer sheet? | SMOG Section 8
4.1.4 | KVA Rating-Does KVA rating match the Loss compensation sheet? | SMOG Section 8
4.1.5 | Are physical high voltage tap settings being used in loss calculations? | SMOG Section 8
4.1.6 | Are physical low voltage tap settings being used in loss calculations? | SMOG Section 8
4.1.7 | Transformer Connection-Is transformer connected Wye or Delta? | SMOG Section 8
4.1.8 | Transformer Phases-Are there one or three phases? | SMOG Section 8
4.1.9 | Meter Elements-Are correct number of elements used in loss calculation? | SMOG Section 8
4.1.10 | Meter Class-Is correct class rating of meter used in loss calculation? | SMOG Section 8
4.1.11 | Meter Voltage Rating-Is secondary meter voltage used in loss calculation? | SMOG Section 8
4.1.12 | Percent Impedance-Is nameplate impedance used in loss calculation? | SMOG Section 8
4.1.13 | Percent Excitation-Does excitation match with transformer data sheet? | SMOG Section 8
4.1.14 | Watt Losses-Does computation of transformer data equal no load watts factor? | SMOG Section 8
4.1.15 | Var Losses-Does computation of transformer data equal no load var factor? | SMOG Section 8
4.1.16 | Watt Losses-Does computation of transformer data produce no load watt factor? | SMOG Section 8
4.1.17 | Var Losses-Does computation of transformer data produce no load var factor? | SMOG Section 8
4.1.18 | Is median tap voltage used in loss calculation? | SMOG Section 8
4.1.19 | Auto-Transformer Compensation-Are iron and copper losses included in compensation factors? | SMOG Section 8
Line Losses
4.2.1 | Line Type-What type of line is used in loss calculation? | SMOG Section 8.4
4.2.2 | Are correct ohms/mile used in loss computations? | SMOG Section 8.4
4.2.3 | Line Distance-How many miles of line are used in loss calculation? | SMOG Section 8.4
4.2.4 | Do compensation values and registration values agree with ERCOT approved TLC spreadsheet? | SMOG Section 3.3.3
4.2.5 | Do EPS meters have correct compensation factors (+ or -) programmed in the meters? | SMOG Section 3.3.3
Current Transformer Equipment and Circuit Validation
Physical Properties
5.1.1 | BIL Rating-Is CT designed and constructed to ANSI C12.11 or IEEE C57.13-1993 standards? | SMOG Section 7.5.1
5.1.2 | Winding Configuration-Does CT winding comply with approved typical configurations? | SMOG Section 7.5.3.1
5.1.3 | Does CT nameplate list the following nameplate items, manufacturer, type of device, serial number, ratios, burden, accuracy class, thermal rating factor, and impulse level? | SMOG Section 7.5.2
5.1.4 | Does nameplate data match submitted Site Certification sheet? | SMOG Section 3.2.3(1)(g)
5.1.5 | Does nameplate rated primary current (ratio and RF) match approved EPS Design proposal? | SMOG Section 7.5.3.2
5.1.6 | Rated Secondary Current(wire wound)-Is secondary current rated at 5 amps for rated primary amps? | SMOG Section 7.5.3.3
5.1.7 | Accuracy Class-Is CT designed for minimum standard accuracy of .3 percent? | SMOG Section 7.5.3.5
5.1.8 | CT Rating Factors-Does CT possess a standard rating factor of 1.0 or higher at operating temperature? | SMOG Section 7.5.3.7
5.1.9 | Short Time Thermal Current Rating-Does CT meet the requirements for short time thermal currents as prescribed in IEEE 57.13? | SMOG Section 7.5.3.8
5.1.10 | Short Time Mechanical Current Rating-Does CT meet the requirements for short time thermal currents as prescribed in IEEE 57.13? | SMOG Section 7.5.3.9
5.1.11 | Fault Withstand-Does existing CT possess ability to withstand available fault current? | SMOG Section 1.3.1
5.1.12 | Insulating Oil-Has oil been tested for Non-PCB's? | SMOG Section 7.5.6
5.1.13 | Does Non-PCB nameplate exist on transformer? | SMOG Section 5.6
5.1.14 | Do test switches allow for the measurement of metered quantities and the application of test values? | SMOG Section 1.2.3
5.1.15 | Rated Output(fiber optic)-Is output 1 amp @ rated primary current and used with class 2 meter? | SMOG Section 7.5.3.4
5.1.16 | Fiber Optic Accuracy & Burden-Does optic CT meet the standard requirement of .3% accuracy while ensuring the burden is not exceeded? | SMOG Section 7.5.3.6
5.1.17 | Fiber connection is maintained to within manufacturers prescribed limits? | SMOG Section 7.5.3.6
CT Quantity
5.2.1 | 4-Wire Wye-Do three CT's exist? | SMOG Section 1.3.2
5.2.2 | 3-Wire Delta-Do two CT's exist? | SMOG Section 1.3.2
Burden
5.3.1 | Is circuit limited to highly accurate billing meters and load control transducers only? | SMOG Section 1.3.4(3)
5.3.2 | Are separate isolated secondaries existing between EPS metering and other allowable meter devices? | SMOG Section 1.5.2(1)(c)
5.3.3 | Is the total burden on the CT within the CT Burden Rating? | SMOG Section 1.3.3(1)
5.3.4 | Annual Burden Test-Demonstrated connected burden check? | SMOG Section 1.3.3(2)
CT Secondary Wiring
5.4.1 | There are no splices in the CT Secondary Wiring? | SMOG Section 1.3.4(1)
5.4.2 | Is wire of sound electrical and mechanical integrity? | SMOG Section 1.3.4(2)
5.4.3 | Has wire integrity inspection been performed within the last three years? | SMOG Section 1.3.4(2)
Grounding of CT Circuit
5.5.1 | Return Conductor-Does each set of CT's have one common return conductor? | SMOG Section 1.3.5(1)
5.5.2 | Grounding Point-Is there only one grounded point of the common return? | SMOG Section 1.3.5(2)
5.5.3 | Ground wire size-Is the ground conductor of the same size as the polarity and common wire? | SMOG Section 1.3.5(4)
Induced Voltages
5.6.1 | Cable Routing-Are cables routed so as to minimize induced voltage effects? | SMOG Section 1.3.6(1)
5.6.2 | Cable Protection-Is suitable protection available (Meter Handbook 10th Edition Chapter 11 pg. 352)? | SMOG Section 1.3.6(2)
Paralleling of CT's
5.7.1 | Nominal Rating-Do all CT's have the same ratio? | SMOG Section 1.3.7(1)(a)
5.7.2 | Phase Connection-Are paralleled CT's connected to the same phases? | SMOG Section 1.3.7(1)(b)
5.7.3 | Secondary connections-Do secondary circuits allow for testing of individual CT's? | SMOG Section 1.3.7(1)(c)
5.7.4 | Are CT's paralleled at the meter test switch? | SMOG Section 1.3.7(1)(c)
5.7.5 | Grounding Point-Is there only one grounded point for the paralleled CT secondaries? | SMOG Section 1.3.7(1)(d)
5.7.6 | Burden Rating-Does each CT possess the ability to support n times the common burden plus its own individual burden within the accuracy class? | SMOG Section 1.3.7(1)(e), and Section 1.3.7(1)(h)
5.7.7 | Common Voltage-Do circuits that have paralleled CT's share a common bus that is normally closed? | SMOG Section 1.3.7(1)(f)
5.7.8 | Is class rating of meter adequate to measure summation of paralleled currents? | SMOG Section 1.3.7(1)(g)
Sizing Current Transformers
5.8.1 | Is CT sized for optimum metering accuracy at peak and minimum loads? | SMOG Section 1.3.8
Voltage Transformer Equipment and Circuit Validation
Physical Properties
6.1.1 | Rated Secondary Voltage-Is secondary output of VT rated at 115/69 volts? | SMOG Section 7.5.4.3
6.1.2 | Accuracy Class-Is VT designed for minimum standard accuracy of .3 percent? | SMOG Section 7.5.4.4
6.1.3 | Thermal Burden Rating-Does VT meet the IEEE C57.13 requirement for thermal burden? | SMOG Section 7.5.4.5
6.1.4 | Insulating Oil-Has oil been tested for Non-PCB's? | SMOG Section 7.5.6
6.1.5 | Does Non-PCB nameplate exist on transformer? | SMOG Section 7.5.6
VT Quantity
6.2.1 | Are there three, phase to ground voltages for 4-wire wye sites? | SMOG Section 1.4.1(1)
6.2.2 | Are there three phase to phase voltages for 3-wire sites? | SMOG Section 1.4.1(2) and SMOG Section 1.4.1(3)
6.2.3 | Burden-Is the total VA burden within nameplate rating for each instrument transformer? | SMOG Section 1.4.2
6.2.4 | Protection-Are fuses of high speed type? | SMOG Section 1.4.3
6.2.5 | Fuses are not installed in the common return or ground circuit? | SMOG Section 1.4.3
VT Secondary Wiring
6.3.1 | Voltage Drop-Is there .3 volt drop or less on secondary? | SMOG Section 1.4.4(1)
6.3.2 | Wire Integrity-Is wire of sound electrical and mechanical integrity with a documented wire integrity inspection within the last three years and if applicable, has the existence of the high/low impedance ground and existence of the fault monitoring system been verified with the last three years? | SMOG Section 1.4.1(4)(a) and SMOG Section 1.4.4(2)
6.3.3 | Have connections of a throw-over relay, if present, been verified to ensure correct voltage phasing is maintained in all operating schemes? | Protocol 10.6.1.1
6.3.4 | There are no splices in the VT Secondary Wiring? | SMOG Section 1.4.4(3)
6.3.5 | Grounding of VT Circuit-Is there only one ground for the set of secondary windings? | SMOG Section 1.4.5(1)
Induced Voltages
6.4.1 | Cable Routing-Are cables routed so as to minimize induced voltage effects? | SMOG Section 1.4.6(1)
6.4.2 | Cable Protection-Is suitable protection available to protect against faults and switching generated voltages? | SMOG Section 1.4.6(2)
6.4.3 | Loss of Potential-Is secondary being monitored for loss of potential for each phase within the required range and time thresholds? | SMOG Section 6.5.4(1)(k)
Three VT-Two CT Metering
New # | Current Transformers
7.1.1 | Are all power transformers primary connections behind the metering point are ungrounded delta, ungrounded wye or phase to phase? | SMOG section 1.3.2
7.1.2 | Has the TDSP verified on an annual basis that all power transformers primary connections behind the metering point are ungrounded delta, ungrounded wye or phase to phase? | SMOG section 1.3.2
7.1.3 | There are no phase-to-ground loads or phase-to-ground sources connected between the metering point and the power transformer primary connections? | SMOG section 1.3.2
7.1.4 | One Line Detail-Does one line detail show all tapped power transformers? | SMOG section 1.3.2
Voltage Transformers
7.2.1 | Are VT's connected delta on secondary? | SMOG Section 1.4.1
7.2.2 | Are there loads connected that provide path for power to ground? | SMOG Section 1.4.1
7.2.3 | Are the VT's connected to the grounding system of the transmission system? | SMOG Section 1.4.1
7.2.4 | Are meter potentials connected phase to common phase? | SMOG Section 1.4.1
7.2.5 | Are secondary of potentials connected the grounding system? | SMOG Section 1.4.1
Notes

## EPS Meter Standards
EPS Site Audit Form Version 6.1 - 1/1/2020
Site: |  |  | Design Proposal Approval Date: |  |  |  | Auditor:
Meter Point: |  |  | Project #: |  |  |  | Audit Date:
| Specific Item Check | Protocol Reference | Resource | Check Method | How Confirmed | Requirement Meet | Comment
EPS Meter Specifications
New # | Measurement Requirement
1.1.1 | Metered Quantities-Do EPS meters possess the ability to measure true four quadrant measurement? | SMOG Section 6.3.1
1.1.2 | Kilovars flowing out of ERCOT-Does EPS meter measure var delivered energy in quadrants 1 & 2? | SMOG Section 6.3.1(1)(b)
1.1.3 | Kilovars flowing into ERCOT-Does EPS meter measure var delivered energy in quadrants 3 & 4? | SMOG Section 6.3.1(1)(c)
Data Recording Function
1.2.1 | Does recorder provide 4 channel recording capability? | SMOG Section 6.3.3(1)(a)
1.2.2 | Memory-Does EPS meter have sufficient memory to store 45 days of 4 channel 15 minute interval data? | SMOG Section 6.3.3(1)(c)
1.2.3 | Memory Capacity-Does IDR count and store at least of 4,000 counts in a single interval? | SMOG Section 6.3.3(1)(d)
1.2.4 | Recording During Communications-Does the meter record interval data while communications session is active, through any port? | SMOG Section 6.3.3(1)(e)
Power Disturbance Functionality
1.3.1 | Retention of Data-During power outage, does meter maintain all data and time/date marks? | SMOG Section 6.3.4(1)(a)
1.3.2 | Does meter resume normal operations upon restoration of power after an outage? | SMOG Section 6.3.4(1)(d)
1.3.3 | Power Outage-Does meter record the time and date of power outage conditions? | SMOG Section 6.3.4(1)(f)
1.3.4 | Does EPS meter have ability to flag intervals when the voltage to the meter power supply is lost for 3 seconds or longer? | SMOG Section 4.4
Test Mode Functionality
1.4.1 | Normal Mode Suspend-During test mode is recording suspended for IDR and normal registers? | SMOG Section 6.3.5(1)(a)
1.4.2 | Test Mode Security-Is meter programmed to limit unauthorized access to test mode? | SMOG Section 6.3.5(1)(b)
1.4.3 | Test Mode Deactivation-Is meter programmed to exit test mode within one hour or less? | SMOG Section 6.3.5(1)(d)
1.4.4 | Compensated Values-For compensated sites, does meter have the capability to display compensated energy values? | SMOG Section 6.4.1
1.4.5 | Self Test-Does meter perform self test for register functionality per the SMOG requirements? | SMOG Section 6.5.1
1.4.6 | Diagnostic Check-In the event of diagnostic failure, does EPS meter store the event that is retrievable by the MDAS? | SMOG Section 6.5.2
1.4.7 | Does meter report pulse overflow if pulses exceed recorder storage capability? | SMOG Section 6.5.3
1.4.8 | Event Logging-Is meter programmed to log all events as listed in SMOG? | SMOG Section 6.5.4
1.4.9 | Local Communications Interface-Does EPS meter possess ability to communicate locally? | SMOG Section 6.6.1
Accuracy Class
1.5.1 | Are EPS meters designed to meet ANSI C12.20, 0.2 accuracy class? | SMOG Section 6.7.1
1.5.2 | Start-up Delay-Does meter begin calculations within 15 seconds of power application to the metering electronics. | SMOG Section 6.7.3
Meter Conformance Requirements
TDSP Approved Meters
2.1.1 | Firmware-Does documentation exist showing the current and pervious versions of firmware along with the dates of deployment, discontinuation, and reasons for discontinuations? | SMOG Section 6.12.2(2)(a)(i)
2.1.2 | Software-Does documentation exist showing the current and pervious versions of software along with the dates of deployment, discontinuation, and reasons for discontinuations? | SMOG Section 6.12.2(2)(a)(ii)
2.1.3 | Certification Letter-Does TDSP possess letter certifying compliance of meter with ANSI/IEC standards and ERCOT Protocols? | SMOG Section 6.12.2(2)(b)
2.1.4 | Test Data-Does TDSP possess document from manufacturer detailing testing certification? | SMOG Section 6.12.2(2)(c) - 6.12.2(2)(c)(g)
1.2.5 | Drawings/Technical Manuals-Does TDSP possess necessary schematics and technical manuals for installation and maintenance of device? | SMOG Section 6.12.2(2)(c) - 6.12.2(2)(c)(g)
Notes