## Slide 1
Further Discussion on Reliability Unit Commitment under Real-Time Co-optimization
David Maggio
RTCTF
June 21, 2019

## Slide 2: Discussion on the Full Ancillary Service (AS) Plan
Reliability Unit Commitment (RUC) is designed to ensure that the system is projected to be able to meet the AS Plan and load forecast
  The AS Plan is typically the MW values posted by ERCOT prior to the start of each year
All products in the AS Plan are part of meeting North American Electric Reliability Corporation (NERC) requirements
The RUC process is ERCOT’s mechanism for meeting NERC requirements
  Regulation is required to meet NERC BAL-001 (control frequency)
  Responsive Reserve Service (RRS) is required to meet NERC BAL-003 (instantaneous loss of 2,750 MW does not trigger under frequency load shed)
  ERCOT Contingency Reserve Service (ECRS) is required to meet NERC BAL-002 (recover frequency within 15 minutes)
  Non-Spinning Reserve (Non-Spin) is required to meet NERC BAL-002 (restore contingency reserve within 90 minutes). Note that Non-Spin quantities are significantly reduced following the implementation of ECRS.
ERCOT continues to work with stakeholders to refine the needed quantities of AS

## Slide 3: RUC Protects the Full AS Plan Today
Today, RUC protects the full AS Plan capacity
AS Responsibility contained within online Resources’ Current Operating Plans (COPs) is protected from dispatch by RUC by high penalty prices
Reserves from offline Resources are inherently protected (i.e., the amount of reserves can’t be decreased or increased)

## Slide 4: RUC with Co-optimization will have Greater Flexibility
In the way ERCOT has presented it, RUC with co-optimization will also protect the full AS Plan but will have the flexibility to move the AS Plan capacity around to avoid the need to commit offline Resources
Enabling RUC to assign ECRS and Non-Spin to offline Resources will reduce the need to RUC for capacity
  Today any Non-Spin Responsibility in online COPs is blocked from dispatch in RUC
  With co-optimization RUC will be able to assign Non-Spin or ECRS to offline Resources
Enabling RUC to assign AS across the fleet will reduce the need to RUC for congestion
  RUC has access to full capacity of Resources with helping shift factors

## Slide 5: Comparison of RUC Today and with Co-optimization
Today
The AS Plan is contained in the COPs and the system’s capacity available to manage system conditions is driven by Resource’s AS limits.
R1
online
Reg.
R4
offline
R2
online
RRS
R3
online
Non-Spin
R1
online
Reg.
R2
online
R3
online
RRS
R4
offline
Non-Spin
Non-Spin assigned to offline R4, avoiding need to commit for capacity.
Capacity on R2 used to avoid need to commit for congestion.
With Co-optimization
The AS Plan is used directly and the system’s capacity to both meet the AS Plan and honor transmission constraints is evaluated using online and offline capability.

## Slide 6: Amount of Qualified AS Capability in the Fleet
It is unlikely that RUC will see a need for AS that is not really being driven by a more general systems capacity shortage
But to meet NERC requirements ERCOT needs RUC to be the backstop tool to check AS capability
Chart: 2018 Daily Minimum Online Capacity Qualified for Regulation Up and RRS
Chart: 2018 Hourly Capacity Qualified for Non-Spin

## Slide 7: Projected AS Capability will be Visible to MPs
With the implementation of Real-Time Co-optimization (RTC), Market Participants will have hourly reports on aggregate AS capability for future hours
  These reports will be based on the information used by RUC to determine commitment recommendations
This report would be similar to today’s Short Term Adequacy Reports and would be in addition to other RUC reports (e.g., the “Deselected Hourly RUC Recommendations”)
With additional reporting and the RUC deferral process remaining in place, Market Participants will have time to respond

## Slide 8: Pricing Outcomes When Only the AS Plan is Being Met
If Real-Time AS Demand Curves (ASDCs) are at least loosely based on the Operating Reserve Demand Curve (ORDC), prices at AS Plan levels are likely to be high
  In the 2019 AS Plan with projected NPRR863 MW levels, the minimum and maximum hourly total AS Plan capacity are approximately 3,700 MW and 5,600 MW, respectively
    Lower MW values typically occur during Summer peak hours
  The shifted ORDC for 2020 at these levels is approximately:
    $3,000/MWh and $600/MWh, respectively, if all ECRS and Non-Spin capacity is offline (because RUC will not require it be online)
    $2,000/MWh and $120/MWh, respectively, if historical patterns in online/offline capacity continue
    $1,500/MWh and $60/MWh, respectively, if all ECRS and Non-Spin capacity is online (an extreme case)
Additionally, floors on energy and AS offers for RUC-committed Resources and the Reliability Deployment Price Adder mitigate the impact of any RUC commitments
These expectations should incent response by the market

## Slide 9: The Pricing Run Mitigates the Impact of RUCs
The current pricing run inherently addresses RUCs for system-wide capacity more effectively than RUCs for congestion
Modifications to the pricing run contained within NPRR904 will fix known flaws in the relaxation process and improve price signals during RUCs for capacity
ERCOT will continue to work with stakeholders to study additional improvements to the pricing run mechanism
  This discussion is currently at the Congestion Management Working Group (CWMG)

## Slide 10: Conclusions
RUC needs to protect the full AS Plan to meet NERC requirements
RUC will be designed to minimize the need to commit offline Resources while still protecting the full AS Plan
RUC with co-optimization will inherently have additional flexibility to avoid committing Resources for either capacity or congestion
Market Participants will see hourly reports of the aggregate AS capability for future hours to help in their decision making
Expected pricing outcomes for when only the AS Plan is being met should incent market response