## Info
Header Information
TDSP | Operator of the Major Transmission Element.
Major Transmission Element (MTE) | Transmission Element which was, or scheduled to be, on outage and has been associated with one or more high congestion(s).
Equip. Type | Equipment Type of the MTE.
kV | Voltage Level of the MTE. High-side voltage for transformers
Congestion Year/Month | Year and Month the associated congestion occurred.
Contingency | Contingency associated with the MTE.
Overload | Overload associated with the MTE.
Source | Source of the information: RT = Based on historical Real-Time congestion, ST = Based on Outage Coordination Studies. ADD = Addition Requests (both Private and Public)
Outage Type | Outage Type is categorized to be either Planned (PL) and Forced (FR, FE, UE, M1, M2, M3)
Cancel | Outage(s) for the specific MTE was Cancelled, Rejected, or Withdrawn.
Removal Requestor | Stakeholder who is requesting to remove the MTE from the list (Organization)
Addition Requestor | Stakeholder who is requesting to add the MTE from the list (Organization)
Reason for Addition | Justification for adding the MTE to the list. Details of the specific scenarios that the MTE may cause high congestion, including but not limited to: 1. ERCOT Load Level: Peak, Off-Peak (or 35GW, 70GW, etc). 2. Any specific regional load condition: High Houston Load, etc. 3. Wind Generation Level: High, Mid, Low, or N/A. 4. Solar Geneartion Level: High, Mid, Low, or N/A. 5. Any specific abnormal transmission equipment status: i.e. 345 kV line from A to B out-of-service, etc. 6. For Private Submissions, any specific generator output level: i.e. Resource A at 300 MW or above, etc. 7. (Optional) PSSE or PowerWorld case if available.
Reason for Removal | Justification for removing the MTE from the list. Usually entails a Transmission Upgrade Project.
OCITF Consensus | Consensus after OCITF meetings.
Decision | Final (TAC) Decision of the Addition/Removal Request for Non-Consensus items.
Discussion Items | Any other information that stakeholder(s) want to discuss during the OCITF meetings.

## Oncor Comments
TDSP | Major Transmission Element (MTE) | Equip. Type | kV | Congestion Year/Month | Contingency | Overload | Source | Outage Type | Cancel | Removal Requestor | Reason for Removal | OCITF Consensus | Decision | Discussion Items | From Acronym | To Acronym | ERCOT Equip Name | ERCOT Contingency ID
ONCOR | Austrop - Sandow Switch (440) | LN | 345 | 2017 | DCKT Sandow Sw to Bell County East Sw | Taylor - Taylor West 138 kV | ADD |  |  | Oncor (Transmission Project Complete) | TPIT 5800: Upgrade the 10.1-mile Hutto Sw. Sta. - Taylor West -Taylor 138kV line using a conductor rated 2071 A or greater. Actual in-service date 12/03/2018. |  |  |  | SNDSW | AUSTRO | 440 | SSNDAU15
ONCOR | Austrop - Sandow Switch (450) | LN | 345 | 2017 | DCKT Sandow Sw to Bell County East Sw | Taylor - Taylor West 138 kV | ADD |  |  | Oncor (Transmission Project Complete) | TPIT 5800: Upgrade the 10.1-mile Hutto Sw. Sta. - Taylor West -Taylor 138kV line using a conductor rated 2071 A or greater. Actual in-service date 12/03/2018. |  |  |  | SNDSW | AUSTRO | 450 | SSNDAU35
ONCOR | Bell County East Switch - Sandow Switch (421) | LN | 345 | 17/2, 17/4 | DCKT Sandow Sw to Austrop 345 kV | Hutto Sw - Taylor West 138 kV | RT, ST | Planned, Forced |  | Oncor (Transmission Project Complete) | TPIT 5800: Upgrade the 10.1-mile Hutto Sw. Sta. - Taylor West -Taylor 138kV line using a conductor rated 2071 A or greater. Actual in-service date 12/03/2018. |  |  |  | SNDSW | BCESW | 421 | SBCESN35
ONCOR | Bell County East Switch - Sandow Switch (431) | LN | 345 | 17/2 | DCKT Sandow Sw to Austrop 345 kV | Hutto Sw - Taylor West 138 kV | RT | Forced |  | Oncor (Transmission Project Complete) | TPIT 5800: Upgrade the 10.1-mile Hutto Sw. Sta. - Taylor West -Taylor 138kV line using a conductor rated 2071 A or greater. Actual in-service date 12/03/2018. |  |  |  | SNDSW | BCESW | 431 | SBCESND5
ONCOR | Cedar Crest Switch- … - Sargent Road 138 kV | LN | 138 | 16/9 | Mountain Creek Ses Unit Unit8 | Industrial Blvd - Compton Street 138 kV | RT | Planned, Forced |  | Oncor (Transmission Project Complete) | TPIT: 13TPIT0059 Cedar Crest - Industrial 138 kV line, Upgrade existing line, actual in service date 04/14/2019 |  |  |  | CDCSW | SATP2 | 3140_A | SLKJSAR8
ONCOR | Comanche Peak Ses - Everman Switch | LN | 345 | 2017 | Comanch Peak Ses to Mitchell Bend 345 kV | Comanch Peak Ses - Wolf Hollow 345 Sw 345 kV | ADD |  |  | Oncor (Transmission Project Complete) | TPIT 44189: Upgrade Wolf Holllow - Comanche Peak 345 kV Line, actual in-service date 12/29/2018 |  |  |  | CPSES | EVRSW | 6063 | SCPSEVR5
ONCOR | Comanche Peak Ses - Johnson Switch (Oncor) | LN | 345 | 17/5, 17/9, 18/4 | Comanche Peak Ses to Mitchell Bend Sw 345 kV | Wolf Hollow 345 Sw - Comanche Peak Ses 345 kV | RT | Planned |  | Oncor (Transmission Project Complete) | TPIT 44189: Upgrade Wolf Holllow - Comanche Peak 345 kV Line, actual in-service date 12/29/2018 |  |  |  | JONSW | CPSES | 140 | SJONCPS5
ONCOR | Comanche Peak Ses - Parker Switch (6016) | LN | 345 | 2017 | Comanch Peak Ses to Johnson Sw & Everman Sw 345 kV | Comanch Peak Ses - Wolf Hollow 345 Sw 345 kV | ADD |  |  | Oncor (Transmission Project Complete) | TPIT 44189: Upgrade Wolf Holllow - Comanche Peak 345 kV Line, actual in-service date 12/29/2018 |  |  |  | CPSES | PKRSW | 6016 | SCPSPKR5
ONCOR | Comanche Peak Ses - Parker Switch (6062) | LN | 345 | 2017 | Comanch Peak Ses to Johnson Sw & Everman Sw 345 kV | Comanch Peak Ses - Wolf Hollow 345 Sw 345 kV | ADD |  |  | Oncor (Transmission Project Complete) | TPIT 44189: Upgrade Wolf Holllow - Comanche Peak 345 kV Line, actual in-service date 12/29/2018 |  |  |  | CPSES | PKRSW | 6062 | SPKREVR5
ONCOR | East Levee Switch - … - Industrial Blvd | LN | 138 | 15/5, 15/6 | DCKT West Levee Sw to 800/900 Network 138 kV | East Levee Sw - Reagan Street 138 kV (3410_A) | RT | Planned |  | Oncor (Transmission Project Complete) | TPIT 16TPIT0061: Norwood - Record Crossing - East Levee 138 kV Line, upgrade existing line, actual in-service date 1/18/2019 |  |  |  | ELVSW | WNTWK | 3570_A | SWNTEL28
ONCOR | Executive Parkway - … - Handley Ses | LN | 138 | 18/5 | DCKT Eagle Mountain Ses - Saginaw Switch 138 kV | Blue Mound - Wagley Robertson 138 kV | RT | Planned, Forced |  | Oncor (Transmission Project Complete) | TPIT 6779: Wagley Robertson - Saginaw 138 kV Double-circuit Line, Upgrade existing line, in service date 12/2018 |  |  |  | BRHT2 | EXPKY | 6435_B | SWHIHL38
ONCOR | Forney Switch - Seagoville Switch | LN | 345 | 19/4 | DCKT Carrollton Northwest - Lewisville Switch 345 kV | Carrollton Northwest - Lakepointe Tnp 138kV | RT | Planned |  | Oncor (Transmission Project Complete) | TPIT 5488: Carrollton Northwest - Lakepointe (TNMP) Upgrade the 2.1 mile, Oncor portion of the 2.4-mile138kV line using a conductor 3200 A or greater. Actual in-service date 03/01/2019. |  |  |  | FORSW | SGVSW | 220_A | SSGVFOR5
ONCOR | Hackberry - … - Irving Beltine Road & Ligget Switch | LN | 138 | 19/4 | DCKT Carrollton Northwest - Lewisville Switch 345 kV | Carrollton Northwest - Lakepointe Tnp 138kV | RT | Planned |  | Oncor (Transmission Project Complete) | TPIT 5488: Carrollton Northwest - Lakepointe (TNMP) Upgrade the 2.1 mile, Oncor portion of the 2.4-mile138kV line using a conductor 3200 A or greater. Actual in-service date 03/01/2019. |  |  |  | HKBRY | DFWBE | 1150_A | SIRVLIG8
ONCOR | Irving Norwood - Norwood Switch | LN | 138 | 18/9 | DCKT Hicks Switch - Alliance & Roanoke Switch 345 kV | Blue Mound - Wagley Robertson 138 kV | RT | Planned |  | Oncor (Transmission Project Complete) | TPIT 6779: Wagley Robertson - Saginaw 138 kV Double-circuit Line, Upgrade existing line, in service date 12/2018 |  |  |  | NORSW | IRVND | NORSW_IRVND | SIRVNO28
ONCOR | Lake Creek Ses Bus #1 (CB 2840, etc.) | BUS | 138 | 15/9 | Waco Mm Mars 2 to Robinson 138 KV, Valley South to Anna Sw & Farmersville Sw 345 kV | Elm Mott - Northcrest Tap 138 kV, Pink Hills Pod - Payne Sw 138 kV | RT, ST | Planned |  | Oncor (Transmission Project Complete) | TPIT 1332: Upgrade the existing 11.5-mile Elm Mott - Waco Northeast Tap 138kV line section using a conductor rated 1794 A or greater. Loop the Elm Mott - Waco Northeast Tap 138kV line section into Northcrest 138kV Substation. Actual in-service date is 11/08/2018. The contingency (Valley South to Anna Sw & Farmersville Sw 345kV) and overload (Pink Hills Pod - Payne Sw 138kV) combination is not valid for this MTE. Also this overloaded element will no longer exist after 2018 due to construction of Stone Creek Switch. |  |  |  | LCSES |  | 4BB1 | N/A
ONCOR | Royse Switch Auto #1 | XF | 345 | 15/9 | Royse Sw Auto FMR3 345/138 KV | Forney Sw - Forney West 138 kV | RT | Planned |  | Oncor (Transmission Project Complete) | TPIT 17TPIT0019: Forney Switch-Royse Switch 138 kV - Upgrade the existing 8-mile Rockwall South - Forney 138kV line using a conductor rated 2071 A or greater, actual in-service date 12/31/2018. |  |  |  | RYSSW |  | FMR1 | SFORRYS5
ONCOR | Sargent Road 345 kV Bus North (CB 7770, etc.) | BUS | 345 | 18/12 | DCKT Venus Switch - Everman Switch 345 kV | Everman Switch 345/138 kV Auto MR2h | RT | Planned |  | Oncor (Transmission Project Complete) | TPIT 6275: Everman 345/138 kV autotransformer - Replace the existing autotransformer #1 and remove autotransformer #2, actual in-service date 12/31/2018. The overloaded element no longer exists. This MTE should be removed from the list. |  |  |  | SAARD |  | BB1N | N/A
ONCOR | Sargent Road 345 kV Bus South (CB 7780, etc.) | BUS | 345 | 18/12 | DCKT Venus Switch - Everman Switch 345 kV | Everman Switch 345/138 kV Auto MR2h | RT | Planned |  | Oncor (Transmission Project Complete) | TPIT 6275: Everman 345/138 kV autotransformer - Replace the existing autotransformer #1 and remove autotransformer #2, actual in-service date 12/31/2018. The overloaded element no longer exists. This MTE should be removed from the list. |  |  |  | SAARD |  | BB1S | N/A
AEP, CROSS, ONCOR | Tesla - … - Tule Canyon (1) | LN | 345 | 16/5, 16/11, 16/12 | Panhandle GTC | N/A | RT, ST | Planned, Forced |  | Oncor (Sunset Criteria) | Panhandle GTC is a basecase constraint so it should be listed under "Overload" column instead of "Contingency" column. No congestion has been observed for this MTE in nearly 3 years. Additionally, the Panhandle GTC documentation indicates a limitation only exists when the double circuit is removed from service and no limitation listed for single circuit outage. |  |  |  | TESLA | CTT_CROS | CROSS_TESLA_1 | SCTTTE45
AEP, CROSS, ONCOR | Tesla - … - Tule Canyon (2) | LN | 345 | 16/5, 16/11, 16/12 | Panhandle GTC | N/A | RT, ST | Planned, Forced |  | Oncor (Sunset Criteria) | Panhandle GTC is a basecase constraint so it should be listed under "Overload" column instead of "Contingency" column. No congestion has been observed for this MTE in nearly 3 years. Additionally, the Panhandle GTC documentation indicates a limitation only exists when the double circuit is removed from service and no limitation listed for single circuit outage. |  |  |  | TESLA | CTT_CROS | CROSS_TESLA_2 | SCTTTE55
ONCOR | White River - Wett_Cottonwood (WHIT_RV_W_CW1) | LN | 345 | 15/12 | Panhandle GTC | N/A | RT | Planned |  | Oncor (Sunset Criteria) | Panhandle GTC is a basecase constraint so it should be listed under "Overload" column instead of "Contingency" column. No congestion has been observed for this MTE in nearly 3 years. Additionally, the Panhandle GTC documentation indicates a limitation only exists when the double circuit is removed from service and no limitation listed for single circuit outage. |  |  |  | WHIT_RVR | W_CW_345 | WHIT_RV_W_CW1 | SWHIW_15
ONCOR | White River - Wett_Cottonwood (WHIT_RV_W_CW2) | LN | 345 | 15/12 | Panhandle GTC | N/A | RT | Planned |  | Oncor (Sunset Criteria) | Panhandle GTC is a basecase constraint so it should be listed under "Overload" column instead of "Contingency" column. No congestion has been observed for this MTE in nearly 3 years. Additionally, the Panhandle GTC documentation indicates a limitation only exists when the double circuit is removed from service and no limitation listed for single circuit outage. |  |  |  | WHIT_RVR | W_CW_345 | WHIT_RV_W_CW2 | SWHIW_25
CROSS, ONCOR | Alibates - Gray | LN | 345 | 16/3, 16/5 | Panhandle GTC, DCKT Alibates to Tule Canyon 345 kV | N/A, Low Voltage in Panhandle area | ST | Planned | Y | Oncor (ST Only) | Issue was initially observed in a study case but has not occurred in real-time. Additionally, studies alone are no longer used by ERCOT as a criteria for adding elements to the seed list. |  |  |  | ALIBATES | CTT_GRAY | ALIBATE_GRAY_1 | SCTTAL15
ONCOR | Alibates - Aj Swope Sharyland Utilities (AJSWOP_ALIBA) | LN | 345 | 17/4 | Panhandle GTC | N/A | ST | Planned |  | Oncor (ST Only) | Issue was initially observed in a study case but has not occurred in real-time. Additionally, studies alone are no longer used by ERCOT as a criteria for adding elements to the seed list. |  |  |  | ALIBATES | AJ_SWOPE | AJSWOP_ALIBA | SWINALI5
ONCOR | Alibates - Aj Swope Sharyland Utilities (AJSWOP_ALIBA2) | LN | 345 | 17/4 | Panhandle GTC | N/A | ST | Planned |  | Oncor (ST Only) | Issue was initially observed in a study case but has not occurred in real-time. Additionally, studies alone are no longer used by ERCOT as a criteria for adding elements to the seed list. |  |  |  | ALIBATES | AJ_SWOPE | AJSWOP_ALIBA2 | SALIAJ_5
ONCOR | Alibates - Grandview Wind Farm | LN | 345 | 15/5 | Isolates Generation | N/A | ST | Planned |  | Oncor (ST Only) | Issue was initially observed in a study case but has not occurred in real-time. Additionally, studies alone are no longer used by ERCOT as a criteria for adding elements to the seed list. |  |  |  | GRANDVW1 | ALIBATES | GV1_LINE | SGRAALI5
ONCOR | Bulldog Su - Elbow | LN | 138 | 16/9 | Moss Sw to Odessa Ehv Sw 345 kV | Trigas Odessa Tap - Odessa Ehv Sw | ST | Planned | Y | Oncor (ST Only) | Issue was initially observed in a study case but has not occurred in real-time. Additionally, studies alone are no longer used by ERCOT as a criteria for adding elements to the seed list. |  |  |  | ELBOW | BULLDOG | ELBOW_BULLDOG | SELBBUL8
ONCOR | Tule Canyon - White River (TULEC_WHIT_R1) | LN | 345 | 15/11 | Panhandle GTC | N/A | ST | Planned | Y | Oncor (ST Only) | Issue was initially observed in a study case but has not occurred in real-time. Additionally, studies alone are no longer used by ERCOT as a criteria for adding elements to the seed list. |  |  |  | TULECNYN | WHIT_RVR | TULEC_WHIT_R1 | SW_CTUL5
ONCOR | Tule Canyon - White River (TULEC_WHIT_R2) | LN | 345 | 15/11 | Panhandle GTC | N/A | ST | Planned | Y | Oncor (ST Only) | Issue was initially observed in a study case but has not occurred in real-time. Additionally, studies alone are no longer used by ERCOT as a criteria for adding elements to the seed list. |  |  |  | TULECNYN | WHIT_RVR | TULEC_WHIT_R2 | SW_CTU35
ONCOR | Tule Canyon Bus #1 (CB TCN7100, etc.) | BUS | 345 | 15/6 | Panhandle GTC | N/A | ST | Planned |  | Oncor (ST Only) | Issue was initially observed in a study case but has not occurred in real-time. Additionally, studies alone are no longer used by ERCOT as a criteria for adding elements to the seed list. |  |  |  | TULECNYN |  | BUS1_NORTH | N/A
ONCOR | Tule Canyon Bus #2 (CB TCN7102, etc.) | BUS | 345 | 15/6 | Panhandle GTC | N/A | ST | Planned |  | Oncor (ST Only) | Issue was initially observed in a study case but has not occurred in real-time. Additionally, studies alone are no longer used by ERCOT as a criteria for adding elements to the seed list. |  |  |  | TULECNYN |  | BUS2_SOUTH | N/A
ONCOR | Windmill Entire Station | ST | 345 | 16/8 | Basecase | Resource Isolation | ST | Planned | Y | Oncor (ST Only) | Issue was initially observed in a study case but has not occurred in real-time. Additionally, studies alone are no longer used by ERCOT as a criteria for adding elements to the seed list. |  |  |  | WINDMILL |  |  | N/A
ONCOR | Alliance - Hicks Switch (106) | LN | 345 | 16/4 | Rosen Heights to Eagle Mountain Compressor 138 kV, Eagle Mountain Ses Auto MR1 345/138 kV, DCKT Eagle Mountain Ses to Saginaw Sw 138 kV | Rosen Heights Tap 2 - Morris Dido 138 kV, Eagle Mountain Ses Auto AX2 345/138 kV, Eagle Mountain Ses - Morris Dido 138 kV | RT, ST | Planned | Y | Oncor (Multiple subsequent outages caused no congestion) | This MTE line was taken out in 07/2017, 02/2019 and no significant congestion reported. |  |  |  | HCKSW | ALLNC | 106_A | SALLHCK5
ONCOR | Calmont Switch- … - Eagle Mountain Ses (6190_A) | LN | 138 | 15/6, 15/7, 17/4 | DCKT Eagle Mountain SES to Parker Sw & Hicks Sw 345 kV, DCKT Eagle Mountain SES to Parker Sw & Hicks Sw 345 kv, DCKT Eagle Mountain to Saginaw Sw 138 kV | Calmont Sw - … - Eagle Mountain Ses (6185), Calmont Sw - … - Eagle Mountain Ses (6190), Eagle Mountain Ses - Morris Dido 138 kV (6265) | RT | Planned, Forced |  | Oncor (Multiple subsequent outages caused no congestion) | TPIT 4253: Eagle Mountain-Calmont 138 kV line, upgrade existing double-circuit line, actual in service date 01/2018. This MTE taken out multiple times in 2017 (June, July, August, September, October, December), 2018 (January, September) and no significant congestion reported. |  |  |  | CMTSW | WSTHL | 6190_A | SWSTWSM8
ONCOR | Carrollton Northwest - … - Plano Tennyson (840_A) | LN | 138 | 16/1, 16/6 | Lewisville Sw Auto FMR2 345/138kV | Fort Worth Sub - West Denton 138 kV | RT | Planned |  | Oncor (Multiple subsequent outages caused no congestion) | Plano Tennyson-…-Carrollton NW 138 kV line segments taken out multiple times in 2017 and 2018. No congestion observed on this constraint. Remove this MTE |  |  |  | CRLNW | CRLFR | 840_A | SSPRCR28
ONCOR | Cedar Hill Switch- Mountain Creek Ses (3200) | LN | 138 | 15/9, 16/10, 16/11, 16/9 | Polk Street to Oak Cliff South 138 KV, Mountain Creek Ses Auto MR1 138/69 kV, DCKT Mountain Creek Ses to Cedar Crest Sw 138 kV, West Levee Sw Auto MR1 345/138 kV, Spur - … - Salt Creek Bepc, Polk Street to Oak Cliff South 138 kV | Cedar Crest Sw - Oak Cliff South 138 kV, Industrial Blvd - Compton Street 138 kV, Cedar Crest Sw - Oak Cliff South 138 kV | RT, ST | Planned, Forced |  | Oncor (Multiple subsequent outages caused no congestion) | Remove Industrial Blvd-Compton Street 138 kV overload due to completion of TPIT: 13TPIT0059 Cedar Crest - Industrial 138 kV line, upgrade existing line, actual in service date 04/14/2019 This MTE was taken out in 12/2017 (single ckt), 02/2018 (dbl ckt), 03/2018 (dbl ckt),12/2018 (dbl ckt), and no significant congestion reported for this MTE. Remove this MTE |  |  |  | CDHSW | MCSES | 3200 | SMCSCDH8
ONCOR | Cedar Hill Switch- Mountain Creek Ses (3210) | LN | 138 | 15/9, 16/10, 16/11, 16/9 | Polk Street to Oak Cliff South 138 KV, Mountain Creek Ses Auto MR1 138/69 kV, DCKT Mountain Creek Ses to Cedar Crest Sw 138 kV, West Levee Sw Auto MR1 345/138 kV, Polk Street to Oak Cliff South 138 kV | Cedar Crest Sw - Oak Cliff South 138 kV, Industrial Blvd - Compton Street 138 kV, Cedar Crest Sw - Oak Cliff South 138 kV | RT, ST | Planned, Forced |  | Oncor (Multiple subsequent outages caused no congestion) | Remove Industrial Blvd-Compton Street 138 kV overload due to completion of TPIT: 13TPIT0059 Cedar Crest - Industrial 138 kV line, Upgrade existing line, actual in service date 04/14/2019. This MTE was taken out in 01/2017(single ckt), 12/2017(single ckt),02/2018 (dbl ckt), 03/2018 (dbl ckt), 12/2018 (dbl ckt), and no significant congestion reported for this MTE. Remove this MTE. |  |  |  | CDHSW | MCSES | 3210_A | SWMRCDH8
ONCOR | Hicks Switch - … - Saginaw Switch (6270) | LN | 138 | 16/2, 16/3, 17/1 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV, Rosen Heights to Eagle Mountain Compressor 138 kV | Eagle Mountain Ses - Morris Dido 138 kV, Rosen Heights Tap 2 - Morris Dido 138 kV | RT, ST | Planned, Forced |  | Oncor (Multiple subsequent outages caused no congestion) | This MTE line was taken out multiple times in later in 2017 and 2018 and no significant congestion reported on these constraints. Remove this MTE |  |  |  | HCKSW | WGROB | 6270_D | SBLMHCK8
ONCOR | Hicks Switch - … - Saginaw Switch (6271) | LN | 138 | 16/2, 16/3, 16/12, 17/1, 16/1, 16/10 | DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV, Rosen Heights to Eagle Mountain Compressor 138 kV, Rosen Heights to Eagle Mountain Compressor, DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV | Eagle Mountain Ses - Morris Dido 138 kV, Rosen Heights Tap 2 - Morris Dido 138 kV, Eagle Mountain Ses - Morris Dido 138 kV | RT, ST | Planned, Forced |  | Oncor (Multiple subsequent outages caused no congestion) | This MTE line was taken out multiple times in 2017 and 2018 and no significant congestion reported on these constraints. Remove this MTE |  |  |  | HCKSW | WGROB | 6271_A | SFSCHC28
ONCOR | Hicks Switch - Roanoke Switch | LN | 345 | 16/4 | Rosen Heights to Eagle Mountain Compressor 138 kV, Eagle Mountain Ses Auto MR1 345/138 kV, DCKT Eagle Mountain Ses to Saginaw Sw 138 kV, Rosen Heights to Rosen Heights Tap 2 | Rosen Heights Tap 2 - Morris Dido 138 kV, Eagle Mountain Ses Auto AX2 345/138 kV, Eagle Mountain Ses - Morris Dido 138 kV | RT, ST | Planned | Y | Oncor (Multiple subsequent outages caused no congestion) | This MTE line was taken out in 09/2016,10/2016,11/2016,02/2018, 01/2019 and no significant congestion reported on these constraints. Remove this MTE |  |  |  | RNKSW | HCKSW | 107 | SHCKRNK5
ONCOR | Wink Sub Auto Fmr1 138/69 kV | XF | 138 | 17/6 | Wink Sub to Wink Tnp 138 kV | Wink Sub Auto MR2L 138/69 kV | RT | Planned |  | Oncor (Multiple outages) Oncor (Multiple subsequent outages caused no congestion) | Multiple outages at Wink in 06/2017 may have caused this overload on the remaining xfmr. This MTE was taken out couple of times later in 2017 and 2018 and no significant congestion reported. |  |  |  | WINKS |  | FMR1 | XWIN389
ONCOR | Culberson Switch - … - Horseshoe Spring Switch & Riverton Switch (6140) | LN | 138 | 18/12, 19/4 | Moss Switch - Odessa Ehv Switch 345 kV, Fort Stockton Plant - Solstice 138 kV | Rio Pecos - Woodward 2 138 kV, Barilla - Fort Stockton Switch 69 kV | RT | Planned, Forced |  | Oncor (Multiple outages) | This MTE is not a primary contributor. Driver of congestion is likely AEP outages in the Fort Stockton Plant area. Additionally, Culberson Loop is defined as a Local Network (LN) and will remain defined as such until the first solar farm is commercially operational on the loop. When Culberson Loop changes from LN to BES then a Remedial Action Scheme is expected to be in place to address constraints in the Culberson Loop. |  |  |  | CULSW | CHILL | 6140_E | SRVRCUL8
ONCOR | Culberson Switch - … - Yucca Drive Switch | LN | 138 | 18/5 | Moss Switch - Yucca Drive Switch 138 kV, North McCamey - Odessa Ehv Switch 345 kV, Odessa Ehv Switch - … - Wolf Switching Station 138 kV | General Tire Switch - Southwestern Portland Tnp 138 kV, Pigcreek - Solstice 138 kV, General Tire Switch - Southwestern Portland Tnp 138 kV | RT | Planned |  | Oncor (Multiple outages) | This MTE is not a primary contributor. The congestion experienced in May of 2018 is due to multiple simultaneous outages in the area: * Moss Switch - Ector Harper 138 kV (04/27-05/15) * Moss Switch - Ector Hillmont (04/30-05/02) * Holt Switch 138 kV South bus (05/01-05/23) * Holt Switch - Goldsmith Amoco POD 138 kV (05/03-05/23) * Midland County Northwest-Grandview Odessa 138 kV (04/21-05/15) * Andrews North - Andrews County South 138 kV (05/15-08/31) Additionally, Culberson Loop is defined as a Local Network (LN) and will remain defined as such until the first solar farm is commercially operational on the loop. When Culberson Loop changes from LN to BES then a Remedial Action Scheme is expected to be in place to address constraints in the Culberson Loop. |  |  |  | CULSW | MVRCK | 6575_D | SCULCDP8
ONCOR | Lindley Ranch Pecos Express - … - Riverton Switch | LN | 138 | 18/5 | Clearfork - Telephone Road 345 kV, Moss Switch - Yucca Drive Switch 138 kV, Odessa Ehv Switch - … - Wolf Switching Station 138 kV | Pigcreek - Solstice 138 kV, Amoco Three Bar Tap - Andrews County South 138 kV, Cheyenne Tap - No Trees Switch 138 kV, General Tire Switch - Southwestern Portland Tnp 138 kV | RT | Planned, Forced |  | Oncor (Multiple outages) | This MTE is not a primary contributor. The congestion experienced in May of 2018 is due to multiple simultaneous outages in the area: * Moss Switch - Ector Harper 138 kV (04/27-05/15) * Moss Switch - Ector Hillmont (04/30-05/02) * Holt Switch 138 kV South bus (05/01-05/23) * Holt Switch - Goldsmith Amoco POD 138 kV (05/03-05/23) * Midland County Northwest-Grandview Odessa 138 kV (04/21-05/15) * Andrews North - Andrews County South 138 kV (05/15-08/31) Additionally, Culberson Loop is defined as a Local Network (LN) and will remain defined as such until the first solar farm is commercially operational on the loop. When Culberson Loop changes from LN to BES then a Remedial Action Scheme is expected to be in place to address constraints in the Culberson Loop. |  |  |  | LDYPD | RVRSW | 6142_G | SRVRLDY8
ONCOR | Riverton Switch - Three Mile Draw Switch | LN | 138 | 18/5 | Clearfork - Telephone Road 345 kV, Moss Switch - Yucca Drive Switch 138 kV | Pigcreek - Solstice 138 kV, Amoco Three Bar Tap - Andrews County South 138 kV, Cheyenne Tap - No Trees Switch 138 kV | RT | Planned, Forced |  | Oncor (Multiple outages) | This MTE is not a primary contributor. The congestion experienced in May of 2018 is due to multiple simultaneous outages in the area: * Moss Switch - Ector Harper 138 kV (04/27-05/15) * Moss Switch - Ector Hillmont (04/30-05/02) * Holt Switch 138 kV South bus (05/01-05/23) * Holt Switch - Goldsmith Amoco POD 138 kV (05/03-05/23) * Midland County Northwest-Grandview Odessa 138 kV (04/21-05/15) * Andrews North - Andrews County South 138 kV (05/15-08/31) Additionally, Culberson Loop is defined as a Local Network (LN) and will remain defined as such until the first solar farm is commercially operational on the loop. When Culberson Loop changes from LN to BES then a Remedial Action Scheme is expected to be in place to address constraints in the Culberson Loop. |  |  |  | RVRSW | TMDSW | 6143 | SRVRTMD8
BRAZOS, ONCOR | Allen Switch- … - Anna Switch | LN | 138 | 19/2 | DCKT Carrollton Northwest - Lewisville Switch 345 kV | Arco - Cooper Creek Substation 138 kV | RT | Planned |  | Oncor (Multiple outages) | This MTE is not a primary contributor. Driver of congestion is likely Carrollton Northwest-Lakepoint outage |  |  |  | ALNSW | ALLEN | 535_A | SMCWANA8
ONCOR | Calmont Switch- … - Eagle Mountain Ses & White Settlement Switch (6185) | LN | 138 | 17/4, 18/2, 19/4 | DCKT Eagle Mountain to Saginaw Sw 138 Kv, DCKT Hicks Switch - Saginaw Switch 138 kV | Eagle Mountain Ses - Morris Dido 138 kV (6265), Eagle Mountain Compressor Station - Eagle Mountain Poi 138 kV | RT | Planned |  | Oncor (Multiple outages) | Remove Eagle Mountain Compressor Station - Eagle Mountain Poi 138 kV overload as it is a radial line. The congestion experienced in 2018 and 2019 is due to multiple simultaneous outages in the area. * Eagle Mountain SES 138 kV west bus (18/2, 19/4) * Roanoke Switch 345 kV bus, auto#1 (19/4) * Handley SES BKR 4140 (19/4) This MTE alone was taken out multiple times in 2017 and 2018 and no significant congestion reported. |  |  |  | CMTSW | WSTHL | 6185_A | SMRSEMS8
ONCOR | Carrollton East - ... - Preston North | LN | 138 | 19/4 | Argyl - … - Lewisville Switch 138 kV | Argyle - Highlands Tap 138 kV | RT | Planned |  | Oncor (Multiple outages) | This MTE is not a primary contributor. Driver of congestion is likely 345kV Roanoke Switch- Lewisville Switch line. |  |  |  | CRLES | PRSTN | 1500_J | SMDWREN8
ONCOR | Cedar Crest Switch- … - West Levee Switch | LN | 138 | 18/5 | DCKT Westmoreland - Cedar Hill Switch 138 kV & Mountain Creek Ses - Fish Creek Switch 69 kV | Saint Augustine Tap 2 - Sargent Road 138 kV | RT | Planned, Forced |  | Oncor (Multiple outages) | It is not a primary contributor. The congestion experienced in May of 2018 is due to the following multiple simultaneous outages in the area. Future outages of this MTE are not expected to cause congestion and the MTE should therefore be removed. * East Levee-West Levee * West Levee Switch-Dealey Street * Compton Street-Industrial * Dealey station rebuild * Cedar Crest Sw-Wall Street double ckt upgrade work |  |  |  | CDCSW | DEALY | 3120_A | SDEAWLV8
ONCOR | Decordova Ses - Everman Switch | LN | 345 | 19/3 | DCKT Comanche Peak Ses - Everman Switch & Johnson Switch 345 kV | Decordova Dam - Hood 13 8 kV | RT | Forced |  | Oncor (Multiple outages) | The congestion experienced in March of 2019 is due to multiple simultaneous outages: Benbrook Switch-Decordova Switch 345 kV, Mitchell Bend Switch-Rocky Creek Switch 345 kV, Decordova-Godley 138 kV. This MTE was outages multiple times (11/2016, 02/2017, 04/2017) and no significant congestion was reported for this MTE. |  |  |  | EVRSW | DCSES | 161 | SDCSEVR5
ONCOR | Hackberry - … - Liggett Switch | LN | 138 | 19/4 | DCKT Carrollton Northwest - Lewisville Switch 345 kV, Argyle - … - Lewisville Switch 138 kV | Carrollton Northwest - Lakepointe Tnp 138kV, Argyle - Highlands Tap 138 kV | RT | Planned |  | Oncor (Multiple outages) | This MTE is not a primary contributor. Driver of congestion is 345kV Roanoke Switch- Lewisville Switch line. Remove Carrollton Northwest - Lakepointe (TNMP) overload due to completion of TPIT 5488: Upgrade the 2.1 mile, Oncor portion of the 2.4-mile138kV line using a conductor 3200 A or greater. Actual in-service date 03/01/2019. |  |  |  | HKBRY | DFWBE | 1140_E | SDFWLI18
ONCOR | Hutto Switch - … - Taylor (Oncor) | LN | 138 | 18/12 | Killeen Switch TRX KLNSW_3_2 345/138 | Killen Switch TRX MR1H 345/138 kV | RT | Planned |  | Oncor (Multiple outages) | This MTE is not a primary contributor. Driver of congestion is 345kV Killeen - Salado Sw double circuit concurrent outages |  |  |  | HUTTO | TLRWT | 1665_A | STRLHUT8
ONCOR | Morrison Lane Switch - … - Northaven Switch | LN | 138 | 19/3 | DCKT Carrollton Northwest - Lewisville Switch 345 kV | Lakepointe Tnp - Jones Street Tnp 138 kV | RT | Planned |  | Oncor (Multiple outages) | This MTE is not a primary contributor. Driver of congestion is 345kV Roanoke - Lewisville Sw. line. |  |  |  | MSLSW | MSHLN | 3850_A | SMSHNH28
ONCOR | Northaven Switch - … - Renner Switch | LN | 138 | 19/3 | DCKT Carrollton Northwest - Lewisville Switch 345 kV | Lakepointe Tnp - Jones Street Tnp 138 kV | RT | Planned |  | Oncor (Multiple outages) | This MTE is not a primary contributor. Driver of congestion is 345kV Roanoke - Lewisville Sw. line. |  |  |  | NHNSW | ALPHA | 3700_B | SBNDKRK8
ONCOR | Parkdale Switch - … - Prairie Creek Switch | LN | 138 | 18/11 | DCKT Carrollton Northwest - Lewisville Switch 345 kV | Arco - Cooper Creek Substation 138 kV | RT | Planned |  | Oncor (Multiple outages) | This MTE is not a primary contributor. Driver of congestion is likely outages at Carrollton Northwest |  |  |  | PRCRK | PDSES | 3655_A | SPRCPDS8
ONCOR | Tri Corner - Watermill Switch | LN | 345 | 18/9 | DCKT Navarro - Watermill Switch 345 kV | Britten Road - Venus Switch 345 kV | RT | Planned |  | Oncor (Multiple outages) | This MTE is not a primary contributor. Driver of congestion is Cedar Hill Switch - Courtland concurrent outage |  |  |  | TRCNR | WTRML | 215 | STRCWTR5
ONCOR | Saginaw Switch - … - Springdale | LN | 138 | 18/6, 18/9, 19/4 | DCKT Eagle Mountain Ses - Saginaw Switch 138 kV, DCKT Hicks Switch - Alliance & Roanoke Switch 345 kV | Blue Mound - Wagley Robertson 138 kV, Eagle Mountain Compressor Station - Eagle Mountain Poi 138 kV | RT | Planned |  | Oncor (Invalid Entry) Oncor (Transmission Project Complete) | Remove Blue Mound - Wagley Roberton overload due to rebuild. TPIT 6779: Wagley Robertson - Saginaw 138 kV Double-circuit Line, Upgrade existing line, in service date 12/2018. Overloaded element is radial line: Eagle Mountain Compressor Station - Eagle Mountain Poi 138 kV is not expected to overload (cause congestion) as it is operated as a radial line. This MTE is a radial line and an outage of this element does not significantly contribute to any congestion. |  |  |  | AMFTP | SAGNA | 6495_C | SSAGAMF8
ONCOR | Cedar Crest Switch- … - Wall Street | LN | 69 | 18/5 | DCKT Westmoreland - Cedar Hill Switch 138 kV & Mountain Creek Ses - Fish Creek Switch 69 kV | Saint Augustine Tap 2 - Sargent Road 138 kV | RT | Planned |  | Oncor (Invalid Entry) Oncor (Multiple outages) | This MTE is a radial line and an outage of this element does not significantly contribute to any congestion. It is not a primary contributor. The congestion experienced in May of 2018 is due to the following multiple simultaneous outages in the area. Future outages of this MTE are not expected to cause congestion and the MTE should therefore be removed. * East Levee-West Levee * West Levee Switch-Dealey Street * Compton Street-Industrial * Dealey station rebuild * Cedar Crest Sw-Wall Street double ckt upgrade work |  |  |  | CDCSW | CMPST | 3890_A | SWALCDC9
ONCOR | Eagle Mountain Ses - … - Saginaw Switch (6265) | LN | 138 | 19/4 | DCKT Hicks Switch - Saginaw Switch 138 kV | Eagle Mountain Compressor Station - Eagle Mountain Poi 138 kV | RT | Planned |  | Oncor (Invalid Entry) | Overloaded element is radial line: Eagle Mountain Compressor Station - Eagle Mountain Poi 138 kV is not expected to overload (cause congestion) as it is operated as a radial line. |  |  |  | EMSES | MRSDO | 6265_A | SRSNEM38
ONCOR | Alibates - Tule Canyon (ALIB_TULE_2) | LN | 345 | 17/1 | Panhandle GTC | N/A | RT | Forced |  | Oncor (Invalid Entry) | This MTE did not exist until 03/14/2017. Completion of this MTE should be sufficient cause to remove this element from the list. Panhandle GTC is a basecase constraint so it should be listed under "Overload" column instead of "Contingency" column. Alibates – Tule Canyon double circuit was out of service for 2 days in May 2018 and did not trigger the million dollar congestion mark. |  |  |  | ALIBATES | TULECNYN | ALIB_TULE_2 | SALITU25
AEP, ONCOR | Clear Crossing - … - Dermott Switch (DMTSW_KIRCHH1) | LN | 345 | 18/4, 18/5, 18/6, 18/7, 18/8, 18/9, 18/11, 18/12 | DCKT Dermott Sw to Scurry County South Switch 345 kV | Knapp - Scurry Chevron 138 kV | RT | Planned | [6 empty] | CLEARCRO | KIRCHHOF | CLEARC_KIRCHH1 | SKIRDMT5
AEP, ONCOR | Clear Crossing - … - Dermott Switch (DMTSW_KIRCHH2) | LN | 345 | 18/4, 18/5 | DCKT Dermott Switch to Scurry County South Sw 345 kV | Knapp - Scurry Chevron 138 kV | RT | Planned | [6 empty] | CLEARCRO | KIRCHHOF | CLEARC_KIRCHH2 | SKIRDM35
AEP, ONCOR, TNMP | Lotebush - … - Yucca Drive Switch | LN | 138 | 18/5 | Fort Stockton Plant - Rio Pecos 138 kV | 16th Street Tnp - Woodward 2 138 kV, Rio Pecos - Woodward 2 138 kV | RT | Forced | [6 empty] | YUCSW | LOTEBUSH | 6332_A | SHACPB38
BRAZON, ONCOR | Carrollton Northwest - … - Collin Ses & Legacy | LN | 138 | 18/11 | DCKT Carrollton Northwest - Lewisville Switch 345 kV | Arco - Cooper Creek Substation 138 kV | RT | Planned | [6 empty] | CRLFR | CRLNW | 815_H | SHBRCR48
BRAZOS, ONCOR | Carrollton Northwest - Lewisville Switch (105_A) | LN | 345 | 2018 | Jones Street Tnp to Lewisville Sw 138 kV | Ti Tnp - West Tnp 138 kV | ADD | [7 empty] | CRLNW | LWSSW | 105_A | SLWSCRL5
BRAZOS, ONCOR | Carrollton Northwest - Lewisville Switch (83) | LN | 345 | 17/3 | Jones Street Tnp to Lewisville Sw 138 kV | Ti Tnp - West Tnp 138 kV | RT | Planned | [6 empty] | CRLNW | LWSSW | 83 | SKRWCR25
LCRA, ONCOR | North McCamey - Odessa Ehv Switch | LN | 345 | 2018 | McCamey GTC | N/A | ADD | Planned | [6 empty] | NORTMC | ODEHV | MCCAMEY_ODESSA | SNORODE5
ONCOR | Airco Tap 2 - ... - Blackland | LN | 138 | 18/5 | Farmersville Switch - Royse Switch (381) | Farmersville Switch - Royse Switch (400) | RT | Planned, Forced | [6 empty] | ACTP2 | WMFPI | 1700_J | STRNNWT8
ONCOR | Allen Switch- Plano Tennyson | LN | 345 | 18/5 | DCKT Carrollton Northwest - Lewisville Switch 345 kV | Jones Street Tnp - Lewisville Switch 138 kV, Carrollton Northwest - Lakepointe Tnp 138kV | RT | Planned, Forced |  |  | Remove Carrollton Northwest - Lakepointe (TNMP) overload due to completion of TPIT 5488: Upgrade the 2.1 mile, Oncor portion of the 2.4-mile138kV line using a conductor 3200 A or greater. Actual in-service date 03/01/2019. |  |  |  | ALNSW | PTENN | 80 | SPTEALN5
ONCOR | Benbrook Switch- Sycamore Creek | LN | 345 | 17/2, 17/3 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV, Lewisville Sw - Jones Street Tnp 138 kV | RT | Forced |  |  | Remove Carrollton Northwest - Lakepointe (TNMP) overload due to completion of TPIT 5488: Upgrade the 2.1 mile, Oncor portion of the 2.4-mile138kV line using a conductor 3200 A or greater. Actual in-service date 03/01/2019. |  |  |  | BNBSW | SYCRK | 6000_A | SSYCEV25
ONCOR | Brownwood - … - Brownwood Switch | LN | 138 | 17/2, 17/3, 17/4, 17/5 | Mercers Gap Sw to Comanche Sw (Oncor) 138 kV | Holder Auto FMR1 138/69 kV, Holder Auto FMR1 138/69 kV | RT, ST | Planned |  |  | Overload element listed twice, remove duplicate entry |  |  |  | BRNSO | BRNWD | 670_A | SBRNCMP8
ONCOR | Brownwood Switch - Goldthwaite | LN | 138 | 18/09 | Ferguson - Sherwood Shores 138 kV | Cedar Valley - Trimmier 138 kV | RT | Planned |  | Oncor (Multiple outages) | The congestion experienced due to several extended LCRA outages in the area. This Oncor MTE was outaged multiple times in 2017(02/16, 03/31) and 2018(12/06, 12/20) and no significant congestion was reported for this MTE. |  |  |  | BRNSW | GOLDTH | 680 | SGOLBRN8
ONCOR | Carrollton Northwest - Lakepointe Tnp | LN | 138 | 19/1, 19/2 | DCKT Carrollton Northwest - Lewisville Switch 345 kV | Arco - Cooper Creek Substation 138 kV | RT | Planned, Forced | [6 empty] | CRLNW | LKPNT | 591 | SLKPCRL8
ONCOR | Carrollton Northwest - Plano Tennyson | LN | 345 | 18/12 | DCKT Carrollton Northwest - Lewisville Switch 345 kV | Arco - Cooper Creek Substation 138 kV | RT | Planned | [6 empty] | CRLNW | PTENN | 81 | SPTECRL5
ONCOR | Cedar Crest Switch - … - Industrial Blvd | LN | 138 | 18/5, 19/3 | DCKT Westmoreland - Cedar Hill Switch 138 kV & Mountain Creek Ses - Fish Creek Switch 69 kV, DCKT Carrollton Northwest - Lewisville Switch 345 kV, Lewisville Switch - Jonesville Tnp 138 kV | Saint Augustine Tap 2 - Sargent Road 138 kV, Carrollton Northwest - Lakepointe Tnp 138kV, Ti Tnp - West Tnp 138 kV | RT | Planned |  |  | Remove Carrollton Northwest - Lakepointe (TNMP) overload and corresponding contingency (DCKT Carrollton Northwest - Lewisville Switch 345 kV) for this MTE due to completion of TPIT 5488: Upgrade the 2.1 mile, Oncor portion of the 2.4-mile138kV line using a conductor 3200 A or greater. Actual in-service date 03/01/2019. Remove TI TNP-West TNP overload and corresponding contingency (Lewisville Switch - Jonesville Tnp 138 kV ) for this MTE as it is remote from the MTE. Keep MTE due to Saint Augustine Tap 2 - Sargent Road 138 kV overload. |  |  |  | CMPST | CDCSW | 3130_A | SCMPIND8
ONCOR | Cedar Hill Switch- Courtland | LN | 345 | 18/9 | DCKT Navarro - Watermill Switch 345 kV | Britten Road - Venus Switch 345 kV | RT | Planned | [6 empty] | CRTLD | CDHSW | 6020_A | SCRTCDH5
ONCOR | Centerville Road Switch- … - Judd Court & Kirkland Park | LN | 138 | 19/3 | DCKT Carrollton Northwest - Lewisville Switch 345 kV | Lakepointe Tnp - Jones Street Tnp 138 kV | RT | Planned | [6 empty] | CNRSW | GRLRD | 3250_A | SLKHCNR8
ONCOR | Centerville Road Switch- Forney Switch | LN | 345 | 2017 | Forney - Royse DCKT | Forney 345/138 auto | ADD | [7 empty] | CNRSW | FORSW | 110 | SCNRFOR5
ONCOR | Comanche Peak Ses - Comanche Switch | LN | 345 | 18/11 | DCKT Brown Switch - Killen Switch 345 kV | Comanche Tap - Comanche Switch 138 kV | RT | Forced | [6 empty] | CMNSW | CPSES | 662 | SCMNCPS5
ONCOR | Courtland - Everman Switch | LN | 345 | 18/5 | DCKT Navarro - Watermill Switch 345 kV | Britten Road - Venus Switch 345 kV | RT | Planned, Forced | [6 empty] | EVRSW | CRTLD | 6020_D | SCRTEVR5
ONCOR | Denton Drive - … - Empire Central & Norwood Switch | LN | 138 | 18/5 | DCKT Carrollton Northwest - Lewisville Switch 345 kV, DCKT Navarro - Watermill Switch 345 kV | Jones Street Tnp - Lewisville Switch 138 kV, Carrollton Northwest - Lakepointe Tnp 138kV, Britten Road - Venus Switch 345 kV | RT | Planned, Forced |  |  | Remove Carrollton Northwest - Lakepointe (TNMP) overload due to completion of TPIT 5488: Upgrade the 2.1 mile, Oncor portion of the 2.4-mile138kV line using a conductor 3200 A or greater. Actual in-service date 03/01/2019. Remove Britten Road - Venus Switch 345 kV Overload and corresponding DCKT Navarro - Watermill Switch 345 kV Contingency for this MTE. Driver of congestion is Courtland - Everman Switch concurrent outage |  |  |  | DENDR | ECTP1 | 3360_A | SEMPNO28
ONCOR | East Levee Switch - West Levee Switch | LN | 138 | 18/5 | DCKT Carrollton Northwest - Lewisville Switch 345 kV | Jones Street Tnp - Lewisville Switch 138 kV, Carrollton Northwest - Lakepointe Tnp 138kV | RT | Planned |  |  | Remove Carrollton Northwest - Lakepointe (TNMP) overload due to completion of TPIT 5488: Upgrade the 2.1 mile, Oncor portion of the 2.4-mile138kV line using a conductor 3200 A or greater. Actual in-service date 03/01/2019. |  |  |  | WLVEE | ELVSW | 4090 | SELVWL28
ONCOR | Elkton - … - Forney Switch | LN | 345 | 2017, 17/11, 18/11, 18/12 | Trinidad - Enterprise and - Stryker DCKT, DCKT Martin Lake Ses - Stryker Creek Ses & Mt Enterprise 345 kV | Elkton 345/138 kV auto, Lufkin Switch - Nacogdoches South Tap 138 kV | ADD, RT | Planned | [6 empty] | ELKTN | TRCNR | 170 | SELKFOR5
ONCOR | Elkton - Martin Lake Ses | LN | 345 | 2017 | Martin Lake - Styker and - Enterprise DCKT | Martin Lake - Shamburger | ADD | [7 empty] | ELKTN | MLSES | 180 | SELKMLS5
ONCOR | Euless - … - Hackberry (745) | LN | 138 | 16/12, 17/3 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Lewisville Sw - Jones Street Tnp 138 kV | RT | Planned | [6 empty] | EULES | GRHWY | 745_H | SCPLHKB8
ONCOR | Euless - … - McKamy Road & Roanoke Switch (1065) | LN | 138 | 16/10, 16/12, 17/1, 17/2, 17/3, 17/4, 17/5, 17/10 | DCKT Carrollton Northwest to Lewisville Sw 345 kV, DCKT Hicks Sw to Alliance & Roanoke Sw 345 kV, DCKT Martin Lake Ses to Elkton & Tyler Grande 345 kV | Carrollton Northwest - Lakepointe Tnp 138 kV, Blue Mound - Wagley Robertson 138 kV, Lewisville Sw - Jones Street Tnp 138 kV, Tyler Northwest - Shamburger Sw 138 kV | RT, ST | Planned |  |  | Remove Carrollton Northwest - Lakepointe (TNMP) overload and its corresponding contingency for this MTE due to completion of TPIT 5488: Upgrade the 2.1 mile, Oncor portion of the 2.4-mile138kV line using a conductor 3200 A or greater. Actual in-service date 03/01/2019. Remove Blue Mound - Wagley Roberton overload due to rebuild and its corresponding contingency for this MTE due to completion of TPIT 6779: Wagley Robertson - Saginaw 138 kV Double-circuit Line, Upgrade existing line, in service date 12/2018 Remove Tyler Northwest - Shamburger Sw 138 kV Overload element as well as DCKT Martin Lake Ses to Elkton & Tyler Grande 345 kV Contingency as it is remote from the MTE. |  |  |  | EULES | GRHWY | 1065_L | SKIMRN48
ONCOR | Forney Switch - Royse Switch (200) | LN | 345 | 2017 | Forney Sw - Centerville Road Sw 345 kV | Forney 345/138 kV Auto MR3 | ADD | [7 empty] | FORSW | RYSSW | 200 | SFORRYS5
ONCOR | Forney Switch - Royse Switch (210) | LN | 345 | 2017 | Forney Sw - Centerville Road Sw 345 kV | Forney 345/138 kV Auto MR3 | ADD | [7 empty] | FORSW | RYSSW | 210 | SFORRY25
ONCOR | Forney West - … - Royse Switch | LN | 138 | 18/5 | Farmersville Switch - Royse Switch (381) | Farmersville Switch - Royse Switch (400) | RT | Planned | [6 empty] | FORWE | RYSSW | 1090_E | SRWARY28
ONCOR | Gresham Road Switch - … - Nacogdoches Se | LN | 138 | 17/12, 18/7, 18/8, 18/10, 18/12, 19/1 | DCKT Martin Lake Ses to Stryker Creek Ses & Trinidad Ses to Mt Enterprise 345 kV, DCKT Mt Enterprise - Trinidad Ses & Martin Lake Ses - Stryker Creek Ses | Herty North Switch - Nacogdoches Se 138 kV, Lufkin Switch - Nacogdoches South Tap 138 kV | RT | Planned | [6 empty] | CSHNG | GRDSW | 1450_F | SNCDCMI8
ONCOR | Gresham Road Switch - Stryker Creek Ses | LN | 138 | 18/6 | DCKT Mt Enterprise - Trinidad Ses & Martin Lake Ses - Stryker Creek Ses | Herty North Switch - Nacogdoches Se 138 kV | RT | Planned | [6 empty] | SCSES | GRDSW | 11010 | SGRDSCS8
ONCOR | Hackberry - … - Norwood Switch (100) | LN | 345 | 16/3, 16/7, 17/3 | DCKT Carrollton Northwest to Lewisville Sw 345 kV | Lewisville Sw - Jones Street Tnp 138 kV | RT | Planned | [6 empty] | HKBRY | VLYRN | 100_A | SNORVLY5
ONCOR | Herty North Switch - Nacogdoches Se | LN | 138 | 18/12 | DCKT Mt Enterprise - Trinidad Ses & Martin Lake Ses - Stryker Creek Ses | Lufkin Switch - Nacogdoches South Tap 138 kV | RT | Planned | [6 empty] | HNRSW | NCDSE | 1170 | SHNRNCD8
ONCOR | Holt Switch - … - Yucca Drive Switch | LN | 138 | 18/4 | Fort Stockton Plant to Re Roserock Solar Plant & Solstice 138 kV | Barilla - Fort Stockton Sw 69 kV, Pig Creek - Solstice 138 kV | RT | Planned | [6 empty] | HLTSW | YUCSW | 6425_A | SGSMPB28
ONCOR | Jewett - Singleton (260_A) | LN | 345 | 2018 | DCKT Gibbons Creek to Singleton 345 kV | Jewett - Singleton 345 kV (240) | ADD | Planned | [6 empty] | JEWET | SNG | 260_A | SSNGJE25
ONCOR | Killeen Switch - Salado Switch (271) | LN | 345 | 18/12 | Killeen Switch TRX KLNSW_3_2 345/138 | Killen Switch TRX MR1H 345/138 kV | RT | Planned | [6 empty] | KLNSW | SALSW | 271 | SKLNSA25
ONCOR | Killeen Switch - Salado Switch (272) | LN | 345 | 18/12 | Killeen Switch TRX KLNSW_3_2 345/138 | Killen Switch TRX MR1H 345/138 kV | RT | Planned | [6 empty] | KLNSW | SALSW | 272 | SKLNSAL5
ONCOR | Lewisville Switch - Roanoke Switch | LN | 345 | 19/3, 19/4 | DCKT Carrollton Northwest - Lewisville Switch 345 kV, Argyle - … - Lewisville Switch 138 kV | Ti Tnp - West Tnp 138 kV, Argyle - Highlands Tap 138 kV | RT | Planned, Forced | [6 empty] | LWSSW | RNKSW | 105_B | SLWSRNK5
ONCOR | Lufkin Switch - … - Nacogdoches Se | LN | 138 | 17/12 | DCKT Martin Lake Ses to Stryker Creek Ses & Trinidad Ses to Mt Enterprise 345 kV | Herty North Sw - Nacogdoches Se 138 kV | RT | Planned | [6 empty] | LFKSW | NCSTP | 1350_E | SNCDNCD8
ONCOR | Martin Lake Ses - Mt Enterprise | LN | 345 | 2017 | Martin Lake - Elktion and Tyler Grande DCKT | Martin Lake - Shamburger | ADD | [7 empty] | MLSES | ENTPR | 360 | SENTMLS5
ONCOR | Martin Lake Ses - Styker Creek Ses | LN | 345 | 2017 | DCKT Martin Lake Ses to Elkton & Tyler Grande 345 kV | Martin Lake Ses - Shamburger Sw 345 kV | ADD | [7 empty] | MLSES | SCSES | 370 | SMLSSCS5
ONCOR | Martin Lake Ses - Tyler Grande | LN | 345 | 2017 | DCKT Martin Lake Ses to Styker Creek Ses & Mt Enterprise 345 kV | Martin Lake Ses - Shamburger Sw 345 kV | ADD | [7 empty] | MLSES | TYGND | 340 | STYGMLS5
ONCOR | Midland County Northwest Switch -… - Moss Switch | LN | 138 | 19/4 | DCKT Odessa - Midessa South Sw & Odessa Ehv Switch 138 kV | Big Three Odessa Tap - Odessa Ehv Switch 138 kV | RT | Planned, Forced | [6 empty] | MCNSW | HISKY | 6463_A | SMOSMCN8
ONCOR | Monticello Ses - Paris Switch | LN | 345 | 2017 | DCKT Paris Sw to Valley Ses & Valley South 345 kV | Paris Sw 345/138 kV Auto MR1 | ADD | [7 empty] | PRSSW | MNSES | 390 | SMNSPRS5
ONCOR | Moss Switch - … - Wolf Switching Station | LN | 138 | 18/5 | Clearfork - Telephone Road 345 kV, Moss Switch - Yucca Drive Switch 138 kV | General Tire Switch - Southwestern Portland Tnp 138 kV, Amoco Three Bar Tap - Andrews County South 138 kV | RT | Planned, Forced | [6 empty] | MOSSW | WLFSW | 6480_A | SWLFECT8
ONCOR | Moss Switch - Odessa Ehv Switch | LN | 345 | 19/4 | DCKT Odessa - Midessa South Sw & Odessa Ehv Switch 138 kV | Big Three Odessa Tap - Odessa Ehv Switch 138 kV | RT | Planned, Forced | [6 empty] | MOSSW | ODEHV | 34600 | SMDLODE5
ONCOR | Moss Switch - Yukon Switch | LN | 138 | 17/9 | Yucca Drive Sw to Wolf Switching Station 138 kV | Andrews County South - Amoco Three Bar Tap 138 kV | RT | Planned | [6 empty] | MOSSW | YKNSW | 14075 | SECNMO28
ONCOR | Mt Enterprise - Trinidad Ses | LN | 345 | 2017 | DCKT Elkton to Forney & Tyler Grande to Tri Corner 345 kV | Elkton 345/138 kV Auto MR3 | ADD | [7 empty] | ENTPR | TRSES | 361 | SENTTR25
ONCOR | Odessa Ehv Switch TRX MR1 345/138 kV | XF | 345 | 18/11 | Moss Switch - Odessa Ehv Switch 345 kV | 16th Street Tnp - Woodward 2 138 kV, Odessa Ehv Switch TRX MR2H 345/138 kV | RT | Planned, Forced | [6 empty] | ODEHV |  | ODEHV MR1 345/138 KV XFMR | XOD2E58
ONCOR | Paris Switch CB_8635 | CB | 345 | 2017 | DCKT Paris Sw to Valley Ses & Valley South 345 kV | Paris Sw 345/138 kV Auto MR1 | ADD | [7 empty] | PRSSW |  | 8635 | N/A
ONCOR | Sargent Road - West Levee Switch 345 kV | LN | 345 | 16/9, 18/11, 18/12 | Mountain Creek Ses Unit Unit8, DCKT Carrollton Northwest - Lewisville Switch 345 kV | Industrial Blvd - Compton Street 138 kV, Arco - Cooper Creek Substation 138 kV | RT | Planned |  |  | Remove Industrial Blvd-Comption Street 138 kV overload and corresponding Contingency (Mountain Creek SES Unit Unit 8) due to completion of TPIT: 13TPIT0059 Cedar Crest - Industrial 138 kV line, upgrade existing line, actual in service date 04/14/2019 |  |  |  | SARRD | WLVEE | 217 | SSARWLV5
ONCOR | Stryker Creek Ses - Trinidad Ses | LN | 345 | 2017 | DCKT Elkton to Forney & Tyler Grande to Tri Corner 345 kV | Elkton 345/138 kV Auto MR3 | ADD | [7 empty] | SCSES | TRSES | 480 | STRSSCS5
ONCOR | Tri Corner - Tyler Grande | LN | 345 | 2017 | DCKT Trinidad Ses to Stryker Creek Ses & Mt Enterprise 345 kV | Elkton 345/138 kV Auto MR3 | ADD | [7 empty] | TRCNR | TYGND | 341 | STYGTRC5
ONCOR | Ward Gulf Tap - Wolf Switching Station | LN | 138 | 18/4 | Yucca Drive Sw to Wink Sub 138 kV | Winkler County 6 Tnp - Wickett Tnp 69 kV, Andrews County South - Amoco Three Bar Tap 138 kV | RT | Planned | [6 empty] | WLFSW | WGLFT | 6545_I | SHSAPB38
ONCOR | Wink Sub - Yucca Drive Switch | LN | 138 | 18/3 | Chevron Has to Wickett & Wink Sub & Wolf Switching Station 138 kV | Winkler County 6 Tnp - Wickett Tnp 69 kV | RT | Planned | [6 empty] | WINKS | YUCSW | 6571 | SWINYUC8
Oncor | Ennis - Wahaxhachie - Sterret | LN | 138 | 2018/11 | ENNIS SWITCH to ENNIS WEST SWITCH LIN _C | ENNIS WEST SWITCH - ENNIS SWITCH 138 kV | RT | Planned |  |  | Change MTE to "Ennis West- Wahaxhachie - Sterrett"
Oncor | Ennis West -Ennis Switch - Trumbull | LN | 138 | 2019/6 | ENNIS SWITCH to ENNIS WEST SWITCH LIN _A | Ennis - Wahaxhachie - Sterret | RT | Planned |  |  | Change MTE from "Ennis West -Ennis Switch - Trumbull" to "Ennis West-Ennis Switch". Remove Trumbull. Change Overload element to "Ennis West- Wahaxhachie - Sterrett"
Oncor | Ennis West -Ennis South | LN | 138 | 2019/4 | WXHCH-WXOCF_69kV & ENWSW-STERT_138kV | Ennis West -Ennis Switch - Trumbull | RT | Planned |  |  | Change Overload element from "Ennis West -Ennis Switch - Trumbull" to "Ennis West-Ennis Switch". Remove Trumbull.