## Slide 1
Updates on 2022 GIC Cases
August 13, 2019
PGDTF Meeting

## Slide 2: Disclaimer
These findings are based on the final model posted on July 10th, 2019.
There may be more updates based on Planning findings throughout the study.

## Slide 3: Substation Coordinates
There were several lines between substations with calculated lengths exceeding the user entered lengths by over 10 miles.
Requests to confirm substation coordinates were sent out to several TSPs and REs.
  We are still waiting on a TSP response as well as several RE responses.
  ERCOT may reach out to TSPs for help with RE substation coordinates.

## Slide 4: Substation Grounding Resistances of 0.0
There are a couple RE stations which have a 0.0 substation grounding resistance
  Requests have been sent out to the RE for corrected grounding resistances.
  ERCOT may reach out to TSPs for help with the RE substation grounding resistance.
  In the case we do not receive corrected grounding resistances from the RE or TSP, ERCOT proposes to use PSSE’s default substation grounding resistance, and would like to get PGDTF feedback on this assumption.

## Slide 5: Buses Not Assigned to a Substation
There are several buses that were not assigned to a substation
  Requests have been sent out to affected TSPs and ERCOT has received updated data that can be applied to AC and DC cases
  We are still in the internal process of resolving the remaining issues

## Slide 6: Supplemental GMD Event – Moving Box Issues Encountered
PSSE V34.6 is the only version that can run the moving box methodology for the Supplemental Event
Maximum effective GIC flows differ significantly between PSSE V34.5.1 and PSSE V34.6.
Latitude and longitude input fields are switched in PSSE V34.6 (eg. PSSE using the longitude value for latitude and vice versa) when using the specified location option for the moving box.
ERCOT has run additional GIC analysis with PowerWorld and found that the results are more comparable with results from PSSE V34.5.1 than PSSE V34.6.

## Slide 7: Supplemental GMD Event – Moving Box Preliminary Findings
Preliminary findings:
  Multiple moving box options were tested with the moving box size defined as 100 km by 500 km. Benchmark event was applied outside of the moving box.
  The maximum effective GIC flows with moving box are very similar to results with the supplemental GMD event applied to the entire ERCOT footprint.

## Slide 8
Questions?