## Slide 1
Brief Review of EEA Events For ROS
(8/13 & 8/15)
Dan Woodfin
Sr. Director, System Operations
9/5/2019

## Slide 2: Overview
August peak demands and EEA days in context
Comparisons of August 12th-16th
August 13 EEA
August 15 EEA
Questions

## Slide 3: Daily Peak Hour Demands
Chart: MW
Higher Demands in August
June was cool and wet
July was warm and dry

## Slide 4: New Peak Days
Chart: MW
| 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | August
Total | 69749.4688 | 71049.9531 | 73090.7734 | 72304.1094 | 73115.3984 | 71646.3984 | 71864.0547 | 74531.4297 | 74181.0312 | 71646.8984 | 70968.9531 | 72777.9297 | 70747.7188 | 71449.7734 | 73796.4688
Will focus in on this week for subsequent slides
New All-Time Peak
New Weekend Peak
EEA Days

## Slide 5: System Load
Chart: MW

## Slide 6: Load Patterns – 13:00-20:00 on 8/12-8/16
Chart: Hours/Minutes

## Slide 7: Hourly Wind and Solar
Chart: MW

## Slide 8: Resource Outages
Chart: MW
Outages Shown are non-IRR Outages

## Slide 9: Difference of Load and Net Load Peak Times
Chart: MW

## Slide 10: Load, Wind, and Outage Differences – 8/12-8/13
Outages Shown are non-IRR Outages
Chart: Load (MW)
| 43689.619027777779 | 43690.635185185187 | 43691.741180555553 | 43692.637569444443 | 43693.639097222222
Load | 73820.7188 | 74324.6484 | 71099.75 | 70852.8281 | 72552.8125
Pad Extra
Pad Solar
Pad Load
Wind | 5758.1826 | 4327.1743 | 3936.4854 | 1988.9999 | 5004.0835
Outages | 3807 | 3282 | 3509 | 4894 | 3957
-1431
+504
-525

## Slide 11: Load, Wind, and Outage Differences – 8/12-8/15
Chart: Load (MW)
| 43689.619027777779 | 43690.635185185187 | 43691.741180555553 | 43692.637569444443 | 43693.639097222222
Load | 73820.7188 | 74324.6484 | 71099.75 | 70852.8281 | 72552.8125
Pad Extra
Pad Solar
Pad Load
Wind | 5758.1826 | 4327.1743 | 3936.4854 | 1988.9999 | 5004.0835
Outages | 3807 | 3282 | 3509 | 4894 | 3957
Outages Shown are non-IRR Outages
-2968
+1087
-3769

## Slide 12: Load, Wind, and Outages at Peak
Chart: Load (MW)
| 43689.698194444441 | 43690.637824074074 | 43692.684652777774 | 43703.701412037037
Load | 74679.0469 | 74427.8125 | 71109.4844 | 74557.9688
Pad Extra
Pad Solar
Pad Load
Wind | 7467.8252 | 4507.1694 | 2789.3376 | 9373.8486
Outages | 3765 | 3282 | 4916 | 4403
16:45
15:18
16:25
16:50

## Slide 13: PRC and Online Reserves (RTOLCAP)
Chart: PRC MW

## Slide 14: System Prices and Load (2pm-6pm)
Chart: 
Load1 | 72096.1719 | 72280.6875 | 72568.8516 | 72741.5859 | 72965.7266 | 73170.9453 | 73219.3203 | 73368.5938 | 73568.4375 | 73627.6797 | 73686.9219 | 73793.0469 | 73876.8594 | 73922.8594 | 73881.7188 | 73908.7266 | 74051.9375 | 74185.4609 | 74196.0078 | 74177.7266 | 74215.2969 | 74271.8672 | 74306.8984 | 74346.1875 | 74459.7266 | 74472.4531 | 74344.3281 | 74352.0859 | 74405.1016 | 74458.1172 | 74481.1328 | 74504.1484 | 74605.0391 | 74578.7812 | 74581.2578 | 74608.125 | 74668.5547 | 74631.1016 | 74634.5391 | 74556.1016 | 74311.6094 | 74341.4688 | 74330.8203 | 74545.7969 | 74640.5078 | 74615.5938 | 74569.5703 | 74546.8438 | 74438.7891 | 74407.7266 | 74393.8906
Load2 | 72386.8438 | 72554.1094 | 72763.5234 | 72951.5625 | 73079.7656 | 73255.4688 | 73422.2266 | 73525.1094 | 73585.5391 | 73645.9688 | 73739.2031 | 73873.4062 | 74009.9609 | 74030.2891 | 74144.5078 | 74187.2422 | 74326.2734 | 74393.3906 | 74383.8125 | 74299.7812 | 74169.1562 | 74096.2812 | 74102.1562 | 74033.1797 | 74049.3594 | 74036.6953 | 73936.7344 | 73948.0234 | 74007.1406 | 74024.2344 | 74157.8594 | 74278 | 74298.7734 | 74375.1328 | 74324.3828 | 74376.8906 | 74355.7969 | 74224.3203 | 74003.7188 | 73941.6797 | 73900.9219 | 73990.4297 | 74019.9922 | 74061.9688 | 73942.0938 | 73909.2188 | 74009.0156 | 74042.3359 | 73828.2344
Load3 | 68222.6094 | 68492.5156 | 68732.1562 | 68711.7109 | 68892.3281 | 69065.8906 | 69351.8125 | 69494.25 | 69652.5234 | 69735.0234 | 69809.9688 | 70017.8047 | 70109.4531 | 70161.3906 | 70265.6641 | 70447.2969 | 70565.5391 | 70688.0234 | 70795.1172 | 70885.3125 | 71005.7656 | 71175.3359 | 71351.2578 | 71384.6953 | 71567.8438 | 71469.3203 | 71581.625 | 71641.2578 | 71535.8516 | 71642.1094 | 71659.7578 | 71711.7812 | 71679.2734 | 71701.9375 | 71877.9531 | 71844.4297 | 71628.1953 | 71558.5469 | 71421.5234 | 71479.0391 | 71405.4531 | 71378.25 | 71279.75 | 71277.5 | 71275.25 | 71198.1484 | 71149.1328 | 70991.3672 | 70753.0703
Load4 | 68805.5078 | 68998.9297 | 69085.5156 | 69301.8594 | 69515.9297 | 69703.2188 | 69868.1641 | 69973.6719 | 70096.0469 | 70172.5703 | 70238.6094 | 70304.6484 | 70363.3711 | 70422.0938 | 70560.9141 | 70654.0078 | 70797.4844 | 70851.9141 | 70822.5234 | 70849.2656 | 70888.1406 | 70927.0156 | 70898.6562 | 70889.8438 | 70914.3047 | 70942.1172 | 70991.8359 | 70972.5859 | 70928.4297 | 70958.1172 | 71003.375 | 71060.8906 | 71076.7227 | 71092.5547 | 71038.7031 | 70968.5234 | 70955.1992 | 70941.875 | 70966.0195 | 70990.1641 | 70910.4219 | 70844.6406 | 70732.0391 | 70530.3594 | 70598.4062 | 70604.6719 | 70531.4375 | 70540.75 | 70464.4375 | 70366.1328 | 70315.6875 | 70326.0312 | 70268.7422 | 70183.0547
Load5 | 70867.8672 | 70938.6797 | 71090.5391 | 71147.4922 | 71238.9688 | 71429.4375 | 71530.6875 | 71687.6484 | 71777.9688 | 71906.3047 | 72014.5625 | 72052.8984 | 72162.9609 | 72214.5781 | 72324.5938 | 72438.375 | 72544.1641 | 72600.2812 | 72613.5859 | 72623.9375 | 72690.3906 | 72821.1328 | 72860.5625 | 72880.2266 | 72830.1562 | 72679.6953 | 72718.2656 | 72749.6953 | 72875.8672 | 72882.9609 | 72897.7422 | 72852.5234 | 72804.1016 | 72736.4141 | 72618.7656 | 72684.5156 | 72611.8828 | 72495.8828 | 72411.1562 | 72358.3125 | 72364.125 | 72380.875 | 72335.3984 | 72272.1875 | 72191.2734 | 72127.8516 | 72177.3594 | 71999.5469
Load

## Slide 15: August 13, 2019 EEA Level 1 Timeline
Time | Events
05:00 | Issued OCN for HE 14 to HE 18
13:50 | Issued Advisory for PRC < 3,000 MW
14:55 | Issued Watch for PRC < 2,500 MW
15:10 | Issued EEA 1 for PRC < 2,300 MW
15:16 | Issued a public appeal for voluntary energy conservation
15:16 | Deployed all 10-min and 30-min ERS (926.30 MW)
15:56 | Recalled 10-min ERS (93.01 MW)
16:02 | Re-deployed all 30-min ERS (10 MW)
16:14 | Recalled 30-min ERS (833.39 MW)
17:00 | Cancelled EEA 1
17:30 | Cancelled Watch
18:00 | Cancelled Advisory and OCN

## Slide 16: Physical Responsive Capability (PRC) – 8/13/19
ERCOT declared EEA Level 1 at 15:10 when the PRC was 2,156 MW.
PRC was under 2,300 MW for 35 minutes.
EEA Level 1 continued for 1 hour and 50 minutes until deployed resources were recovered and reserves sustained an upward trend.
EEA Level 1
PRC < 2,300 MW
15:10
17:00
Minimum PRC:
2,025 MW @ 15:14

## Slide 17: Frequency and RRS Deployment - 8/13/19
Chart: Hz
System Frequency dropped to 59.941 Hz at 15:13.
Frequency was restored after deploying additional RRS.

## Slide 18: August 15, 2019 EEA Level 1 Timeline
Time | Events
05:00 | Issued OCN for HE 14 to HE 18
13:30 | Issued Advisory for PRC < 3,000 MW
15:00 | Issued Watch for PRC < 2,500 MW
15:05 | Declared EEA 1 for PRC < 2,300 MW
15:15 | Issued a public appeal for voluntary energy conservation
15:11 | Deployed 30-min ERS (715 MW)
15:30 | Sent VDI for Emergency Energy across the Railroad DC Tie to ERCOT
15:53 | Sent VDIs to keep two generators online for HE16 and HE17
16:54 | Recalled all 30-min ERS
17:05 | Terminated EEA 1
17:15 | Ended VDI for Emergency Energy across the Railroad DC Tie
17:35 | Cancelled Watch
18:00 | Cancelled Advisory and OCN

## Slide 19: Physical Responsive Capability (PRC) – 8/15/19
ERCOT declared EEA Level 1 at 15:05 when the PRC was 2,245 MW.
PRC was under 2,300 MW for 26 minutes.
EEA Level 1 continued for 2 hours until deployed resources were recovered and reserves sustained an upward trend.
EEA Level 1
PRC < 2,300 MW
15:05
17:05
Minimum PRC:
2,134 MW @ 15:18

## Slide 20: Frequency and RRS Deployment - 8/15/19
Chart: Hz
System Frequency dropped to 59.944 Hz at 14:50.
Frequency was restored after deploying RRS.

## Slide 21: Questions?