## Slide 1
NOGRR 195
Freddy Garcia
September 6, 2019

## Slide 2: NOGRR 195
Texas RE Audit Recommendation
  NERC VAR-001-5 R5.2 and NERC VAR-002-4.1 R2
    Recommended to clarify expectations for notification requirements for Voltage Set Point deviations (whether adhering to an existing Voltage Set Point or responding to a new Voltage Set Point).
  Current language in Section 2 of Operating Guides is too vague
    RE shall “as soon as practicable” notify QSE, TO and/or ERCOT if unable to comply with a VSS or Voltage Set point Instruction
  Propose clear and measureable expectation while not promoting an unnecessary time delay in the communication
    “as soon as practicable, but no longer than 10 minutes”
      Paragraphs (2) and (3) of Section 2.2.10
      Paragraphs (3) and (4) of Section 2.7.3.5
  Clarify expectation that a QSE/RE must respond to a new Voltage Set Point even if within the tolerance band
    Aligns with ROS approved language in NPRR 849

## Slide 3: Operating Limits and AVR coordination
Operating Guide 2.7.3.1
AVR setting may need to be coordinated with other Generation Resources.
Propose that AVR settings support deploying full reactive capability prior to going beyond the tolerance bands.
Nominal Voltage | Normal Operating Limits | Emergency Operating Limits
345 | 327.75 – 362.25 | 310.5 – 379.5
230 | 218.5 – 241.5 | 207 – 253
138 | 131.1 – 144.9 | 124.2 – 151.8
115 | 109.25 – 120.75 | 103.5 – 126.5
69 | 65.55 – 72.45 | 62.1 – 75.9

## Slide 4: Voltage Set Point tolerances
Currently Voltage Set Point tolerances, +/- 2%, can be more than a 14 kV spread for Generation Resources connected to 345kV POI’s.
  Difficult to maintain reliability when Resource allowed to drift far from set point.
  Using whole numbers easier for operators to determine when out of range rather than having to calculate a band that changes dynamically because of being in %.
  NPRR 776 implemented common point of measurement eliminating metering differences between the TO and GR.
Nominal Voltage | Tolerance Band KV
345 | +/- 3kV
230 | +/- 3kV
138 | +/- 2kV
115 | +/- 2kV
69 | +/- 1kV