## Slide 1
NPRR 966 ROS
Stephen Solis
System Operations Improvement Manager
ERCOT Public
September 5, 2019

## Slide 2: Problem Statement
The integration of renewable generation within the ERCOT interconnection has introduced several new Transmission Operators and fundamentally altered the generation dispatch pattern in the region.
A new tool is needed to address multiple interrelated objectives of coordination of voltage and reactive control between TOs, maintaining reliability by preventing and or correcting System Operating Limit (SOL) exceedances, minimizing cost of maintenance resulting from increased switching, and maintaining or improving transfer capability both in real time and in operations planning timeframe.

## Slide 3: Reactive Power Coordination “Tool”
ERCOT is actively working on a project to develop a multi hour look ahead tool to improve reactive power coordination within the ERCOT region.
This tool will be called the Reactive Power Coordination (RPC) tool.
The RPC tool will optimize reactive power controls (shunt devices, Generator Voltage Set Points, Static Var Compensators (SVCs), etc.) across a multi-hour interval to resolve reactive power and voltage-related constraints (voltage limits, temporal constraints*, reactive reserves, etc.) under both normal and contingency conditions.
*Temporal constraints are time based constraints (e.g. How often you can switch each reactive device in a certain time period).

## Slide 4: Reactive Power Coordination “Tool”
The RPC tool will be used in several studies looking ahead.
  Hourly study that optimizes across the next 12 hours.
  Daily study that optimizes the same window as Daily Reliability Unit Commitment (DRUC) .
  Incorporated into operations look ahead studies
  Offline planning study mode that will work with bus branch cases (e.g. SSWG).

## Slide 5: RPC Output Mock-up Screenshot

## Slide 6: Reactive Power Coordination “Tool” benefits
Fewer real time voltage limit exceedances
Help to ensure that sufficient reactive reserves are maintained
Fewer real time Constraint Management Plans (CMPs) and more identified in advance of real time.
Improved reactive flows (e.g. lower MVAR flows in some areas, fewer areas with circulating MVAR flows, etc.)
Enhanced coordination between TOs
Allows for more realistic and reliable future look ahead studies

## Slide 7: Time Frame
ERCOT would like to have NPRR 966 make the December 2019 Board meeting to support finalization of planning activities in 2019.
Preliminary scheduling estimates would make production capability sometime mid-2021. This schedule will be finalized by end of 2019.
ERCOT expects to test or pilot results for 3 to 6 months to tune, stabilize and build confidence in the reactive dispatch prior to un gray boxing NPRR 966 language.

## Slide 8: Coordination between ERCOT and TOs
Project Implementation
  Coordinate on necessary constraints for the RPC tool (e.g. temporal constraints)
  Coordinate on necessary “cost”/weighting factors for control selection in the RPC Tool (i.e. prioritizing which reactive devices should be utilized in what sequence)
  Coordinate on the RPC tool reactive dispatch output file design
Rule Changes
  Coordinate and implement NPRR 966
  Gray boxed until project goes live
Testing
  Manual review of RPC tool reactive dispatch for issues
  Pilots and tests of implementing actual RPC tool reactive dispatch

## Slide 9: Impact on Generators
Voltage Set Point changes
  Some generators may see an increase and some generator may see a decrease in the number of Voltage Set Point changes which depends on the topology and reactive controls in an area.
  Generator Voltage Set Point changes will be given a higher control “cost” in the optimization engine so that Transmission reactive devices are utilized first up to a combined “cost” that exceeds the “cost” of the Voltage Set Point change.
  Generators will still receive Voltage Set Point changes the same way as today from their ERCOT Transmission Operator even if the change was part of the optimized reactive dispatch.

## Slide 10: NPRR 966 – Outage Coordination
Sections 3.1.4.3 and 3.1.4.4 clarifies expectations for entering Outages for reactors, capacitors, reactive controlled sources for Resource Entities and TSPs so that the Reactive Power Coordination tool can have accurate awareness of the availability of the reactors, capacitors, and reactive controlled sources;

## Slide 11: NPRR 966 – Modeling
Sections 3.10.7.1.4 and Section 3.10.7.1.5 specify the need to add temporal constraints to the Network Operations Model for transformers and reactive devices so that the Reactive Power Coordination tool can have accurate awareness of any temporal constraints of the reactors, capacitors, or other reactive controlled sources (e.g. how many times a capacitor can be switched in or out in a 12 hour period); and
This will be similar to the information received as part of a survey in 2017.

## Slide 12: NPRR 966 – Voltage Support Service
Paragraph (7) added to Section 6.5.7.7 for ERCOT to provide the hourly optimized reactive power dispatch via a TSP-specific Messaging System and also to post the schedule on the MIS Secure Area accessible by the TSPs.
This Messaging System will operate very similarly to the one utilized with Qualified Scheduling Entities (QSEs) but will be for TSPs. This will require the TSPs to implement an application programming interface (API) on the TSP side to interface with the Messaging System.
The TSPs will be responsible for providing this Dispatch schedule to their operators.
The TSPs will also be required to send an acknowledgement of receipt each hour.
The TSPs would be required to implement and or instruct others to implement the Dispatch schedule unless they determine they should not due to reliability reasons (e.g. a Forced Outage occurs that modifies the necessary reactive Dispatch or the inability to implement the Dispatch, severe weather, etc.).
ERCOT will be required to notify the TSPs when the Reactive Power Coordination tool is unavailable and when it becomes available again.

## Slide 13: Discussion / Q&A