| NOGRR Number | 184 | NOGRR Title | Related to NPRR919, Exemption from Governor Primary Frequency Response Control for Certain Resources in Private Use Networks |
| --- | --- | --- | --- |
| Date of Decision | September 5, 2019 |
| Action | Rejected |
| Timeline | Normal |
| Proposed Effective Date | Not applicable |
| Priority and Rank Assigned | Not applicable |
| Nodal Operating Guide Sections Requiring Revision | 2.2.7, Turbine Speed Governors 2.2.8, Performance/Disturbance/Compliance Analysis |
| Related Documents Requiring Revision/Related Revision Requests | Nodal Protocol Revision Request (NPRR) 919, Exemption from Governor Primary Frequency Response Control for Certain Resources in Private Use Networks |
| Revision Description | This Nodal Operating Guide Revision Request (NOGRR) aligns the Nodal Operating Guide with changes proposed in NPRR919 that allows a Resource in a Private Use Network whose primary function is providing steam to a host, and is not participating in the ERCOT energy market, to be exempted from Primary Frequency Response service requirements. The Governor will still be in service, but may be allowed to be in pressure control instead of Primary Frequency Response control. |
| Reason for Revision | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |
| Business Case | This NOGRR aligns Nodal Operating Guide language with revisions proposed to the Nodal Protocols in NPRR919. |
| ROS Decision | On 2/8/19, ROS unanimously voted to table NOGRR184 and refer the issue to the Performance, Disturbance, Compliance Working Group (PDCWG). All Market Segments were present for the vote. On 9/5/19, ROS unanimously voted to reject NOGRR184. All Market Segments were present for the vote. |
| Summary of ROS Discussion | On 2/8/19, participants requested additional information from the PDCWG regarding the practice of Resources showing a High Sustained Limit (HSL) of zero for extended periods of time. On 9/5/19, participants reviewed discussions at the 8/8/19 ROS meeting regarding NOGRR184, noting that the majority of PDCWG members did not support the request for exemption. |

| Sponsor |
| --- |
| Name | Eric Woelfel |
| E-mail Address | ewoelfel@fpcusa.com |
| Company | Formosa Utility Venture, Ltd |
| Phone Number | 973-716-7389 |
| Cell Number | 973-634-6107 |
| Market Segment | Independent Generator |

| Market Rules Staff Contact |
| --- |
| Name | Phillip Bracy |
| E-Mail Address | Phillip.Bracy@ercot.com |
| Phone Number | 512-248-6917 |

| Comments Received |
| --- |
| Comment Author | Comment Summary |
| Formosa 032219 | Modified language to further restrict proposed exemption exclusively to simple cycle steam turbine Generation Resources |

Market Rules Notes

Please note that the baseline language in the following sections has been updated to reflect the incorporation of the following NOGRRs into the Nodal Operating Guides:

- NOGRR185, Related to NPRR921, RTF-2 Elimination of the Terms All-Inclusive Generation Resource and All-Inclusive Resource (incorporated 7/1/19)

  - Section 2.2.7

  - Section 2.2.8

Proposed Guide Language Revision

2.2.7	Turbine Speed Governors

(1)	A Governor shall be in-service whenever the All-Inclusive Generation Resource is connected to the ERCOT Transmission Grid.

[NOGRR185: Replace paragraph (1) above with the following upon system implementation of NPRR921:] (1) A Governor shall be in-service whenever the Generation Resource or Settlement Only Generator (SOG) is connected to the ERCOT Transmission Grid.

(2)	Generation Resources that have not been evaluated in at least eight Frequency Measurable Events (FMEs) within 36 months shall conduct Governor performance tests for that Generation Resource within 12 months using one of the test methods or historical methods specified in Section 8, Attachment C, Turbine Governor Speed Tests.  The Resource Entity shall then provide test results to ERCOT.  Specific Private Use Network Generation Resources that have been granted an exemption per paragraph (2) of Nodal Protocol Section 8.5.1.1, Governor in Service, will be excused from conducting Governor performance tests.

(3)	All-Inclusive Generation Resources, except steam turbines of Combined Cycle Generation Resources, shall have a Governor droop characteristic and Governor Dead-Band setting no greater than those shown below in Table 1, Maximum Governor Dead-Band Settings, and Table 2, Maximum Governor Droop Settings, as defined below:

Table 1: Maximum Governor Dead-Band Settings

| Generator Type | Max. Deadband |
| --- | --- |
| Steam Turbines with Mechanical Governors | +/- 0.034 Hz |
| Hydro Turbines with Mechanical Governors | +/- 0.034 Hz |
| All Other Generating Units/Generating Facilities | +/- 0.017 Hz |
| Controllable Load Resources (CLRs) | +/- 0.036 Hz |

Table 2: Maximum Governor Droop Settings

| Generator Type | Max. Droop % Setting |
| --- | --- |
| Combustion Turbine (Combined Cycle) | 4% |
| All Other Generating Units/Generating Facilities/ CLRs | 5% |

[NOGRR185: Replace paragraph (3) above with the following upon system implementation of NPRR921:] (3) Generation Resources, except steam turbines of Combined Cycle Generation Resources, Settlement Only Transmission Generators (SOTGs), and Settlement Only Transmission Self-Generators (SOTSGs) shall have Governor droop characteristics and Governor Dead-Band settings no greater than those shown below in Table 1, Maximum Governor Dead-Band Settings, and Table 2, Maximum Governor Droop Settings, as defined below: Table 1: Maximum Governor Dead-Band Settings Generator Type Max. Deadband Steam Turbines with Mechanical Governors +/- 0.034 Hz Hydro Turbines with Mechanical Governors +/- 0.034 Hz All Other Generating Units/Generating Facilities +/- 0.017 Hz Controllable Load Resources (CLRs) +/- 0.036 Hz Table 2: Maximum Governor Droop Settings Generator Type Max. Droop % Setting Combustion Turbine (Combined Cycle) 4% All Other Generating Units/Generating Facilities/ CLRs 5%

(4)	If ERCOT determines that ERCOT System reliability would be enhanced, for a defined period of time, ERCOT may direct Wind-powered Generation Resources (WGRs) under the control of a Remedial Action Scheme (RAS) to limit power increases due to frequency if there is risk of an RAS operation due to a low frequency FME.

2.2.8	Performance/Disturbance/Compliance Analysis

(1)	Performance/Disturbance/Compliance analysis shall be performed by ERCOT for the purpose of ensuring conformance with the Protocols and Operating Guides.  All All-Inclusive Generation Resources and Controllable Load Resources, except nuclear-powered Resources, specific Private Use Network Generation Resources granted an exemption by ERCOT under paragraph (2) of Nodal Protocol Section 8.5.1.1, Governor in Service, or WGRs with a permanent exemption approved by ERCOT, must respond to frequency disturbances with a Governor droop as specified in Section 2.2.7, Turbine Speed Governors. Each All-Inclusive Generation Resource and Controllable Load Resource based on participation in at least eight FMEs, shall meet a minimum 12-month rolling average initial Primary Frequency Response performance and sustained Primary Frequency Response performance of 0.75 as calculated in Section 8, Attachment J, Initial and Sustained Measurements for Primary Frequency Response.  When assessing conformance with the Protocols and Operating Guides, ERCOT shall evaluate the annual rolling average and may exclude from the performance analysis All-Inclusive Generation Resources or Controllable Load Resources in accordance with, but not limited to, the following conditions:

(a)	Operating within the larger of five MW or 2% of the High Sustained Limit (HSL) or the maximum capacity for low frequency disturbances;

(b)	Operating within the larger of five MW or 2% of the HSL or the maximum capacity above the LSL for high frequency disturbances;

(c)	For any Generation Resource carrying power augmentation, the maximum capacity will be computed as the HSL minus Non-Frequency Responsive Capacity (NFRC); or

(d)	Having a technical or physical limitation filed with the ERCOT client representative and approved by ERCOT.

[NOGRR185: Replace paragraph (1) above with the following upon system implementation of NPRR889:] (1) Performance/Disturbance/Compliance analysis shall be performed by ERCOT for the purpose of ensuring conformance with the Protocols and Operating Guides. All Generation Resources, SOTGs, SOTSGs, and Controllable Load Resources, except nuclear-powered Resources or WGRs with a permanent exemption approved by ERCOT, must respond to frequency disturbances with a Governor droop as specified in Section 2.2.7, Turbine Speed Governors. Each Generation Resource, SOTG, SOTSG, and Controllable Load Resource based on participation in at least eight FMEs, shall meet a minimum 12-month rolling average initial Primary Frequency Response performance and sustained Primary Frequency Response performance of 0.75 as calculated in Section 8, Attachment J, Initial and Sustained Measurements for Primary Frequency Response. When assessing conformance with the Protocols and Operating Guides, ERCOT shall evaluate the annual rolling average and may exclude from the performance analysis Generation Resources, SOTGs, SOTSGs, or Controllable Load Resources in accordance with, but not limited to, the following conditions: (a) Operating within the larger of five MW or 2% of the High Sustained Limit (HSL) or the maximum capacity for low frequency disturbances; (b) Operating within the larger of five MW or 2% of the HSL or the maximum capacity above the LSL for high frequency disturbances; (c) For any Generation Resource carrying power augmentation, the maximum capacity will be computed as the HSL minus Non-Frequency Responsive Capacity (NFRC); or (d) Having a technical or physical limitation filed with the ERCOT client representative and approved by ERCOT.

(2)	Market Participants shall request an exemption from, or correction of, performance during an FME within 30 days of the MIS posting date of the “Initial and Sustained Frequency Response Unit Performance” report.

(3)	ERCOT will, on an as needed basis, utilize the Performance, Disturbance, Compliance Working Group (PDCWG) as a technical resource in providing input for types of technical or physical limitations that may be approved by ERCOT.

(4)	ERCOT shall make a regular report on selected system disturbances, documenting the response of individual Generation Resources and Controllable Load Resources.  In addition, Resource Entities, QSEs, and individual members of the PDCWG are encouraged to work within their respective companies to enhance the performance of individual Generation Resource’s or Controllable Load Resource’s control systems through application of the results of the PDCWG studies.