## Slide 1
2019 RRS Study Scope Update
ERCOT
Operations Planning
PDCWG | September 11th, 2019

## Slide 2: 2019 RRS Study Scope
  Event Benchmark
  To ensure the accuracy of dynamic models used in RRS study, ERCOT will conduct a new study to benchmark the model performance against historical large events. EROCT will compare the simulated frequency response at the system level with the actual event frequency profile. Event details are summarized below:
  RRS Mix Study
    To have a better understanding of PFR resource mix post coal retirement, ERCOT will conduct a statistic analysis to determine if it is necessary to redistribute the PFR responsibility between coal and gas units in the provision of 1150 MW PFR.
 | Event Time | MW Loss | Inertia | Load | Wind
No.1 | 11/25/2017 20:24 | 1,228MW | 186.4GWs | 35,122 MW | 8,370 MW
No.2 | 9/1/2017 21:46 | 1,209 MW | 290.3 GWs | 47,534 MW | 4,333 MW
No.3 | 3/2/2019 3:18 | 1,224 MW | 211.9 GWs | 33,942 MW | 6,833 MW

## Slide 3
Divider Slide
Divider Slide (optional)
Event Benchmarking

## Slide 4: Event: 11/25/2017 20:24
Chart: Frequency
 | All governors enabled | 21 governors disabled
# of governors | 151 | 130

## Slide 5: Event: 9/1/2017 21:46
Chart: Frequency
 | All governors enabled | 70 governors disabled
# of governors | 192 | 122

## Slide 6: Event: 3/2/2019 3:18
Chart: Frequency
 | All governors enabled | 11 governors disabled
# of governors | 169 | 158

## Slide 7
Divider Slide
Divider Slide (optional)
RRS Resource Mix

## Slide 8: RRS Mix Study
Chart: 2018 RRS Mix Breakdown
| inertia<250 GWs | inertia>=250 GWs
Gas% | 0.73286 | 0.85322
Coal% | 0.26714 | 0.14678
Current Practice in RRS Methodology :
Inertia <250 GWs, 70%Gas+30%Coal
Inertia >=250 GWs, 85%Gas+15%Coal
Based on 2018 data, no change will be made to RRS mix assumptions in 2019 RRS study.