## Slide 1
Sep 16, 2019
WMWG Meeting
ERCOT Staff
Resource Limit Calculator Telemetry Validation Considerations

## Slide 2: Recap
At the Jun 24, 2019 WMWG meeting ERCOT provided an overview of the current telemetry validations in the Resource Limit Calculator (RLC).
  Slide Deck: Link
  At this meeting, Stakeholders requested ERCOT to holistically review the validations in RLC and identify any changes that would better align these to current operational standards.

## Slide 3: Normal/Emergency Ramp Rate Telemetry
Current
If Suspect data quality is detected for resource ramp rates, then effective ramp rate is computed using the resource specific ramp rate curves as submitted in the resource’s Market Manager Generation Resource Parameters or Resource Asset Registration Form (RARF) if there was no Market Manager Submission
Possible Change
Modify ERCOT internal procedures to update the low reasonability limit for telemetered ramp rates in ERCOT’s SCADA to be 0 for all resources irrespective the submitted low reasonability ramp limit in the market system or RARF.
When a suspect data quality is detected for resource ramp rates, retain the last telemetered value which had good quality instead of switching to market ramp rates.

## Slide 4: Possible New Alarm for Invalid QSE Telemetry
When sudden “large” changes in System level markers like HDL-GEN, HASL-GEN etc. are detected, explore if impacts on actual frequency can be used to determine if the changes are valid and related to an operational condition or indicative of invalid telemetry from QSE(s).
  This condition when detected would raise an alarm, which will trigger post analysis.
  As the detection of invalid data using this logic becomes more robust, functionality maybe extended and other actions may be included as a part of this logic.

## Slide 5: Offline status with non-zero MW output
Current
Following conditions will trigger RLC to ramp down a resource per its SCED down ramp rate
  MW > 0.9*LSL and resource status is one of (OFF, OUT, EMR, OFFNS, EMRSWGR)
Explore the following approach
Enhance this logic check to ensure that the only time a Resource is dispatched, per its SCED down ramp rate, is when there is sufficient indication that the MW telemetry is unreasonable. In all other conditions, Resource will be locked at its current output (i.e., MW = LDL = HDL).

## Slide 6: Startup/Shutdown Sequence
Current
No special logic exists to ensure a resource follows a proper startup/shutdown sequence i.e. Off – Startup – ON or ON – Shutdown – OFF.
Explore the following approach
Explore additional logic to ensure startup/shutdown sequence is being followed appropriately and use this to derive how dispatch limits should be set when inconsistent telemetry is detected.

## Slide 7: Resource Status Telemetry
Current
When a Generation Resource telemeters a Resource Status code that is reserved for Load Resource/Controllable Load Resource (ex. OUTL), the dispatch limits continue to be calculated based on the dispatch limit logic (i.e. the Resource may be expected to move based on its ramp rate).
Change to be implemented in October 2019 release
When a Generation Resource telemeters a Load Resource only Resource Status, lock the Resource at its current output (i.e., MW = LDL = HDL). And vice versa.

## Slide 8
Discussion

## Slide 9
June 24, 2019
WMWG Meeting
ERCOT Operations
Current Telemetry Validations in Resource Limit Calculator

## Slide 10: RLC Overview
Protocol Section 6.5.7.2 drives the calculations and monitoring built into RLC today.
RLC executes every 4 seconds.
RLC uses telemetry from QSEs to compute limits such as HDL, LDL, HASL and LASL. These limits are then sent to MMS/SCED.
  RLC runs several sanity checks against input telemetry data and weeds out inconsistencies in telemetered data using pre-established business rules.
Resource Limit Calculator
Ancillary Service Calcs.
ex. HASL, LASL
Resource Limit Calcs.
ex. SURAMP, SDRAMP, HDL, LDL
GTBD Calculation
Includes PLDRR, PWRR
Telemetry from QSE via SCADA/ICCP
Dispatch Data from MMS
Operator Initiated Data
SCED BP/LMP Data To QSE via SCADA/ICCP
Calculated and telemetered Data To MMS/SCED
Data For Settlements
Data For Reports and Compliance
Other Calcs.
Ex. SCED Trigger following RRS release

## Slide 11: Telemetry Validations in RLC – SCADA Quality Check
RLC has logic to handle telemetry SCADA data qualities of Good, Suspect, Manual Replaced and Uninitialized. (“intra”-telemetry checks)
If any resource specific telemetry data (excluding ramp rate related telemetries) from QSE has Suspect quality, then RLC retains the last good value which had telemetered quality Good and does not consider the new value of the telemetry that has Suspect data quality
  Thus, if bad data quality is detected for LSL or HSL, the last good value would be used.
If Suspect data quality is detected for resource ramp rates, then effective ramp rate is computed using the resource specific ramp rate curves as submitted in the resource’s Market Manager Generation Resource Parameters or Resource Asset Registration Form (RARF) if there was no Market Manager Submission

## Slide 12: Telemetry Validations in RLC – Data Check
The second layer of validation in RLC are is to ensuring telemetry data consistency across two or more resource specific telemetries. (“inter” telemetry checks)
Following conditions will trigger RLC to set HDL=LDL=MW
  HSL < LSL
  LSL < 0
  HSL <= 0 AND resource status is not one of the offline statuses*
  HSL < Non-Spin Responsibility and resource status is OFFNS
  (HSL – LSL) < Sum of AS Responsibility and resource status is not OFFNS
  Resource Status has invalid value but good SCADA quality
Following conditions will trigger RLC to ramp down a resource per its SCED down ramp rate
  MW > 0.9*LSL and resource status is one of (OFF, OUT, EMR, OFFNS, EMRSWGR)
Alarms are issued in case of most of the telemetry checks outlined above.
* offline statuses = NA, OUT, OFFNA, OFF, EMR, OFFQS, EMRSWGR OR FRRSUP

## Slide 13: Resource Limit Calculator Logic Example 1
- Telemetered HSL = 0
Input Values | MW or #
High Sustainable Limit (HSL) | 0
Power Output (MW) | 500
Normal Down Ramp Rate | 200
Resource Status Code | 3 (ON)
Sum of AS Responsibilities | 0
Low Sustained Limit (LSL) | 0
Calculated Values | MW
High Dispatch Limit (HDL) | 500
Low Dispatch Limit (LDL) | 500
500
- LDL=HDL=BP=500
- Actual Unit Capacity
Output Values | MW or #
Base Point (BP) | 500
Overridden Resource Status Code | 
RLC Logic Applicable:
  Following conditions will trigger RLC to set HDL=LDL=MW
    HSL<=0 AND resource status is not one of the offline statuses*
EMS Alarms triggered:
  Alert: TEL HSL BELOW 0
550

## Slide 14: Resource Limit Calculator Logic Example 2
- Telemetered HSL = 0
Input Values | MW or #
High Sustainable Limit (HSL) | 0
Power Output (MW) | 500
Normal Down Ramp Rate | 200
Resource Status Code | 13 (OFF)
Sum of AS Responsibilities | 0
Low Sustained Limit (LSL) | 0
Calculated Values | MW
High Dispatch Limit (HDL) | 300
Low Dispatch Limit (LDL) | 300
Output Values | MW or #
Base Point (BP) | 300
Overridden Resource Status Code | 0 (NA)
500
- LDL=HDL=BP=300
- Actual Unit Capacity
RLC Logic Applicable:
  Following conditions will trigger RLC to ramp down a resource per its SCED down ramp rate
    MW>0.9*LSL and resource status is one of (OFF, OUT, EMR, OFFNS, EMRSWGR)
EMS Alarms triggered:
  Alert: TEL HSL BELOW 0
  Alert: INCONSIST RST AND MW
550

## Slide 15: Resource Limit Calculator Logic Example 3
- Telemetered HSL = 0
Input Values | MW or #
High Sustainable Limit (HSL) | 0
Power Output (MW) | 500
Normal Down Ramp Rate | 200
Resource Status Code | 0 (NA)
Sum of AS Responsibilities | 0
Low Sustained Limit (LSL) | 0
Calculated Values | MW
High Dispatch Limit (HDL) | 300
Low Dispatch Limit (LDL) | 300
Output Values | MW or #
Base Point (BP) | 300
Overridden Resource Status Code | 
500
- LDL=HDL=BP=300
- Actual Unit Capacity
RLC Logic Applicable:
  HDL formula. No Special logic
EMS Alarms triggered:
  Alert: TEL HSL BELOW 0
  Alert: INCONSIST RST AND MW
550

## Slide 16
Discussion

## Slide 17: Resource Specific Telemetry From/To QSE* - Current
To QSE |  | 
Unit Related |  | A/S Related
Base Point (BP) |  | Non-Spin Deployed (NDPL)
Locational Marginal Price (LMP) |  | RRS Deployed (RDPL) [NCLR]
Curtailment (SBBH) |  | 
SCCT Status (SCCT) |  | 
Updated Desired BP (UDBP) |  | 
From QSE |  |  | 
Unit Related |  |  | A/S Related
High/Low Sustained Limits (HSL, LSL) | AVR Status (AVR) |  | FRRS Up/Down Participation Factor (FUPF, FDPF)
High/Low Emergency Limit (HEL, LEL) | Dynamically Scheduled Resource Schedule (DSRS)[Gen] |  | FRRS Up/Down Responsibility (FURS, FDRS)
Normal Up/Down Ramp Rate (NURR, NDRR) | Lower/Raise Block Status (LBST, RBST) [Gen] |  | Regulation Up/Down Participation Factor (RUPF, RDPF)
Emergency Up/Down Ramp Rates (EURR, EDRR) | PSS Status (PSS) |  | Regulation Up/Down Responsibility (RURS, RDRS)
Net MW/MVAR (MW (aka NPF for CCP), MVAR) | POI kV Measurement/Target (KVM, KVT) |  | Responsive Reserve Responsibility/Schedule (RRRS, RRSC)
Gross MW/MVAR (GMW, GMV) | Scheduled Power Consumption (SPC, SPC2) [CLR] |  | High Set Under Frequency Relay (HSUF) [NCLR]
Resource Status (RST) | Storage Resource Charge/Discharge Data (MXCP, MXDP, MXOD, SOC) |  | Non-Spin Responsibility/Schedule (NSRS, NSSC)
CCP Config No (CCC) | IRR MET Data (DEG, IRAD, MPH, PRES, PTMP, TEMP) |  | 
Non Frequency Responsive Capacity (NFRC) | IRR Turbine/Panel Availability (NTOF, NTON, NTUN) |  | 
Load Resource Breaker Status (LRCB) [NCLR] |  |  | 
Max/Low Power Consumption (MPC, LPC) [CLR, NCLR] |  |  | 
*Refer to the ERCOT Nodal ICCP Communications Handbook
http://www.ercot.com/services/rq/re

## Slide 18: Generation Resource Status Codes
  NA (0)
  OUT (11)
  OFFNS (12)
  OFF (13)
  EMR (14)
  OFFQS (19)
  EMRSWGR (20)
  ONRUC (1)
  ONREG (2)
  ON (3)
  ONDSR (4)
  ONOS (5)
  ONOSREG (6)
  ONDSRREG (7)
  ONTEST (8)
  ONEMR (9)
  ONRR (10)
  SHUTDOWN (15)
  STARTUP (16)
  FRRSUP (17)
  ONOPTOUT (18)
*Refer to the ERCOT Nodal ICCP Communications Handbook Section 4.5.2 for more information on Resource Status Codes: http://www.ercot.com/services/rq/re

## Slide 19: RLC Ancillary Service and Dispatch Calculations
HASL
HDL
LDL
LASL

## Slide 20: Alarms from RLC
RLC issues the followings alarms as a result of its data sanity checks.
  HSL – LSL is < AS RESP
  Alert: TEL HSL BELOW 0
  Alert: TEL LSL BELOW 0
  Alert: INVALID HSL SUM
  Alert: SCEDURR BELOW 0
  Alert: INVALID CC CONFIG
  Alert: SUSPECT TEL HDL=LDL=MW
  Alert: INVALID TEL HSL OR LSL
  Alert: INVALID TEL RST
  Alert: INCONSIST RST AND MW