| NPRR Number | 919 | NPRR Title | Exemption from Governor Primary Frequency Response Control for Certain Resources in Private Use Networks |
| --- | --- | --- | --- |
| Date |  | March 22, 2019 |  |
| Submitter’s Information |  |  |  |
| Name |  | Eric Woelfel |  |
| E-mail Address |  | ewoelfel@fpcusa.com |  |
| Company |  | Formosa Utility Venture, Ltd. |  |
| Phone Number |  | 973-716-7389 |  |
| Cell Number |  | 973-634-6107 |  |
| Market Segment |  | Independent Generator |  |

Comments

A change was needed to further restrict the exemption request to only simple cycle steam turbines and to further define what was meant by zero High Sustained Limit (HSL) and not providing Primary Frequency Response support.

Revised Cover Page Language

| Revision Description | This Nodal Protocol Revision Request (NPRR) allows a simple cycle steam turbine Resource in a Private Use Network whose primary function is providing steam to a host, and is not participating in the ERCOT energy market, to be exempted from Primary Frequency Response service requirements. The Governor will still be in service, but may be allowed to be in pressure control instead of Primary Frequency Response control. |
| --- | --- |

Market Rules Notes

Please note the baseline Protocol language in the following section(s) has been updated to reflect the incorporation of the following NPRR(s) into the Protocols:

- NPRR863, Creation of ERCOT Contingency Reserve Service and Revisions to Responsive Reserve (incorporated 3/1/19)

  - Section 8.5.1.1

Revised Proposed Protocol Language

8.5.1	Generation Resource and QSE Participation

8.5.1.1	Governor in Service

(1)	At all times an All-Inclusive Generation Resource is On-Line, its Governor must remain in service and be allowed to respond to all changes in system frequency except during startup, shutdown, or testing.  A Generation Entity may not reduce Primary Frequency Response on an individual All-Inclusive Generation Resource even during abnormal conditions without ERCOT’s consent (conveyed by way of the Resource Entity’s Qualified Scheduling Entity (QSE)) unless equipment damage is imminent.  All All-Inclusive Generation Resources that have capacity available to either increase output or decrease output in Real-Time must provide Primary Frequency Response, which may make use of that available capacity.  Only Generation Resources providing Regulation Up (Reg-Up), Regulation Down (Reg-Down), Responsive Reserve (RRS), or Non-Spinning Reserve (Non-Spin) from On-Line Resources, as specified in Section 8.1.1, QSE Ancillary Service Performance Standards, shall be required to reserve capacity that may also be used to provide Primary Frequency Response.

[NPRR863: Replace paragraph (1) above with the following upon system implementation:] (1) At all times an All-Inclusive Generation Resource is On-Line, its Governor must remain in service and be allowed to respond to all changes in system frequency except during startup, shutdown, or testing. A Generation Entity may not reduce Primary Frequency Response on an individual All-Inclusive Generation Resource even during abnormal conditions without ERCOT’s consent (conveyed by way of the Resource Entity’s Qualified Scheduling Entity (QSE)) unless equipment damage is imminent. All All-Inclusive Generation Resources that have capacity available to either increase output or decrease output in Real-Time must provide Primary Frequency Response, which may make use of that available capacity. Only Generation Resources providing Responsive Reserve (RRS), Regulation Up (Reg-Up), Regulation Down (Reg-Down), ERCOT Contingency Reserve Service (ECRS), or Non-Spinning Reserve (Non-Spin) from On-Line Resources, as specified in Section 8.1.1, QSE Ancillary Service Performance Standards, shall be required to reserve capacity that may also be used to provide Primary Frequency Response.

[NPRR863: Insert paragraph (2) below upon system implementation and renumber accordingly:] (2) All-inclusive Generation Resources that do not have an RRS or Regulation Service Ancillary Service Resource Responsibility shall set their Governor Dead-Band no greater than ±0.036 Hz from nominal frequency of 60 Hz. An All-Inclusive Generation Resource that widens its Governor Dead-Band greater than what is prescribed in Nodal Operating Guide Section 2.2.7, Turbine Speed Governors, must update its Resource Registration data with the new dead-band value.

(2)	At ERCOT’s sole discretion, any simple cycle steam turbine Generation Resource in a Private Use Network that is solely used for providing steam and has a zero High Sustained Limit (HSL) as shown in the Current Operating Plan (COP) for at least 24 months may be granted an exemption from having the Governor in Primary Frequency Response service.  The Governor may instead have the option of being in pressure control service, which does not provide Primary Frequency Response.  This specific Generation Resource would also not be permitted to participate in any Ancillary Service market.  The requesting Generation Resource should submit to ERCOT an attestation and supporting evidence showing the HSL for the requesting Generation Resource was zero for at least 24 months.  ERCOT shall make a determination on the exemption within 60 days of receipt of the attestation.