## Slide 1
Ancillary Service Methodology
Preliminary Quantities for 2020
Sep 16, 2019
WMWG
ERCOT Staff

## Slide 2: Schedule for Stakeholder Discussion
Sep 11, 2019 – PDCWG (Visit 1)
Sep 16, 2019 – WMWG (Visit 1)
Sep 19, 2019 – OWG
Oct 09, 2019 – PDCWG (Visit 2)
Oct 21, 2019 – WMWG (Visit 2)
Nov 06, 2019 – WMS
Nov 07, 2019 – ROS
Nov 20, 2019 – TAC
Dec 10, 2019 – BOD

## Slide 3: Scope of Discussion
ERCOT is not recommending any changes to the methodologies for determining Responsive Reserve Service (RRS) and Non Spin Service quantities for 2020. ERCOT is proposing one change in the methodology for determining Regulation quantities for 2020.
The Ancillary Service (A/S) quantities for 2020 contained in this presentation are based on the methodology that was approved in December 2018.
  The quantities for 2019 reflect moving forward the historic data on which these are based, unless otherwise noted.
  Spreadsheets that contain the associated quantities for January through August of 2019 have been posted on the meeting page for this meeting.
ERCOT is seeking stakeholder feedback for changes to the 2020 A/S Methodology.

## Slide 4
Regulation

## Slide 5: Regulation Service Methodology – 2020
ERCOT is proposing to compute and publish Regulation quantities by month in six separate blocks covering four hour intervals for 2020
  The four hours interval grouping is similar to RRS and Non Spin A/S.
The preliminary Regulation quantities for January 2020 thru August 2020 in subsequent slides have been computed using current methodology (2018 and 2019 five-minute net load variability) and updated Wind Adjustment tables.

## Slide 6: Wind Adjustment Tables - 2020

## Slide 7: Regulation Up January

## Slide 8: Regulation Up March

## Slide 9: Regulation Up August

## Slide 10: Regulation Down January

## Slide 11: Regulation Down March

## Slide 12: Regulation Down August

## Slide 13: Hourly Average Regulation Comparison

## Slide 14
NPRR 968
ERCOT’s Resource Contingency Criteria for BAL-003

## Slide 15: NPRR 968 Update to ERCOT MSSC
ERCOT is updating the MSSC value from the former value of 1,375 MW to 1,430 MW more accurately reflect the expected impact of the loss of either of the South Texas Project nuclear generating units.
This is based on additional information received from NRG and analysis of instantaneous max gross MW data from last five years. A 25 MW margin was applied on the maximum gross capability of any one unit observed in the past five years to derive the new MSSC.

## Slide 16: Potential New Resource Contingency Criteria (RCC)
Current BAL-003 standard establishes ERCOT’s RCC to be 2750 MW (largest G-2 event). With the updated expected impact from the loss of both of the South Texas Project nuclear generating units ERCOT’s RCC may need to be changed
Below is analysis of instantaneous coincidental gross MW data from the last five years the highest coincidental gross MW were observed in Spring, Fall and Winter 2014. The highest coincidental gross MW was observed to be around 2804 MW in March 2014.
Total Gross MW |  |  |  | 
 | Spring | Summer | Fall | Winter
Max | 2803.7 | 2756.9 | 2801.7 | 2802.2
98th Percentile | 2797.6 | 2747.8 | 2797.4 | 2799.1
95th Percentile | 2792.1 | 2742.6 | 2790.8 | 2798.0
90th Percentile | 2780.5 | 2737.1 | 2783.5 | 2796.2
75th Percentile | 2766.6 | 2728.5 | 2761.2 | 2791.6
50th Percentile | 2722.2 | 2718.2 | 2724.4 | 2786.4
25th Percentile | 1391.8 | 2707.2 | 1923.6 | 2781.9
Min | 994.9 | 1372.0 | 1353.8 | 1236.4

## Slide 17
Responsive Reserve Service

## Slide 18: Responsive Service Methodology (RRS) - 2020
The preliminary RRS quantities for January 2020 thru August 2020 in subsequent slides have been computed using 2018 and 2019 system inertia conditions and RRS table updated in 2017.

## Slide 19: RRS January

## Slide 20: RRS February

## Slide 21: RRS March

## Slide 22: RRS April

## Slide 23: RRS August

## Slide 24: Hourly Average RRS Comparison

## Slide 25
Non Spin Reserve

## Slide 26: Non Spinning Reserve Methodology (Non-Spin) - 2020
The preliminary Non-Spin quantities for January 2020 thru August 2020 in subsequent slides have been computed using current methodology (2017, 2018 and 2019 Net load and Net load Forecast) and updated Wind Over-Forecast Error Adjustment tables.

## Slide 27: Wind Over-Forecast Error Adjustment Table - 2020
Wind Over-Forecast Error Adjustment Table track estimated increase in wind over forecast error per 1000 MW increase in installed Wind capacity.
  This table has been updated for 2020.
Average hourly increase in Wind Forecast error per 1000 MW increase in installed Wind capacity = 40 MW
Notes: Average Hourly increase in 2018 = 45 MW

## Slide 28: Non-Spin January

## Slide 29: Non-Spin February

## Slide 30: Non-Spin March

## Slide 31: Non-Spin July

## Slide 32: Non-Spin August

## Slide 33: Hourly Average Non-Spin Comparison

## Slide 34
Suggestions?