| Principle Number | 1.3 | Principle Title | Offering and Awarding Ancillary Services in Real-Time |
| --- | --- | --- | --- |
| Date Posted |  | September 12, 2019 |  |
| Executive Summary |  | Real-Time Co-Optimization (RTC) will allow Qualified Scheduling Entities (QSEs) to offer and be awarded Ancillary Services (AS) in Real-Time. |  |
| Principle Description |  | The purpose of Key Principle 1.3, Offering and Awarding Ancillary Services in Real-Time is to outline the key mechanisms and timelines for submitted AS Offers, as well as those considered and awarded under RTC. Specifically, this principle addresses the following concepts: (a) AS Offer structure and timing; (b) QSE telemetry for updating available capacity from AS Offers; (c) Under-frequency relay (UFR) Load Resource scheduling for Responsive Reserve (RRS) UFR and ERCOT Contingency Reserve Service (ECRS); (d) On-Line hydro Generation Resource (hydro Generation Resources not operating in ONRR mode) scheduling for RRS, Non-Spinning Reserve (Non-Spin), and ECRS; and (e) Constraints to be used for the RTC clearing process. |  |
| RTCTF Discussion |  | On 6/21/19, ERCOT provided a presentation and whitepaper discussing constraint formulation for RTC. There was specific discussion on KP1.3 subsections (1), (2), and (4). On 7/12/19, RTCTF discussed comments that ERCOT received, and ERCOT provided a presentation looking at telemetered ramp rates and constraints for Combined Cycle Generation Resources (CCGRs). On 8/9/19, South Texas Electric Cooperative Inc. (STEC) presented proposed changes to KP1.3, with a focus on the treatment of hydro Resources (subsection (3)). ERCOT also presented on a number of topics related to KP1.3, including discussion on subsections (5) through (9). On 8/27/19, ERCOT continued presentations on KP1.3, including subsection (9). ERCOT staff also presented material introducing KP1.3 subsections (10) through (13). |  |
| TAC Action Requested |  |  |  |
| TAC Action Summary |  |  |  |
| ERCOT Opinion |  |  |  |
| Board Action Requested |  |  |  |
| Board Action Summary |  |  |  |

Proposed Principle Language

# Principle Concepts for TAC Endorsement

None

# Principle concepts Previously Endorsed by TAC

None

# Principle Concepts in DisCussion at RTCTF

- QSEs will have ability in Real-Time to indicate whether a Resource is temporarily unable to provide AS due to operational constraints. When a Resource is unable to provide AS due to operational constraints that Resource’s energy Base Point must be set at the current MW output because the inability to provide AS also would indicate that the Resource is unable to move its energy dispatch. {RTC TF should discuss in this condition, whether the Resource should be removed from the calculation of PRC given that its reserves are “unavailable”}

- UFR Load Resources will be able to self-provide RRS UFR and ECRS; the amount of which will based on Day-Ahead Market (DAM) and AS trades.

- On-Line hydro Generation Resources not operating in ONRR mode will be able to maintain RRS, Non-Spin, and ECRS on those Resources through modification of the Mitigated Offer Cap (MOC).

- RTC will account for frequency responsive capacity of a Combined Cycle Generation Resource (CCGR) when awarding Regulation and RRS Primary Frequency Response (PFR).

- RTC will not change limitations on sub-categories of AS products (e.g., FRRS, FFR, and RRS and ECRS provided via UFR).

- Off-Line Resources providing Non-Spin that are in startup due to a manual deployment of Non-Spin by ERCOT will continue to be eligible for being awarded Non-Spin for the first 25 minutes following the deployment.  The eligible capacity will be based on the High Sustained Limit (HSL) of the Resource less its Base Point instruction.

- Resources operating in quick-start mode that are in startup due to a deployment from ERCOT will continue to be eligible for being awarded ECRS and Non-Spin.  The eligible capacity will be based on the HSL of the Resource less its base point instruction.

- During each execution, RTC awards for energy (Base Points) and AS will be based on taking a fresh look at the pool of Resources available to provide energy and AS.

  - Energy awards (Base Points) will be relative to Resource capability (limits, ramp rates).

  - AS awards will be relative to Resource capability (limits, ramp rates, etc.) and the ASDCs irrespective of the quantity of AS already being deployed.

- Within RTC, ERCOT operators will have the ability to manually mitigate the amount of AS being awarded to Resources that, when deployed, may violate transmission constraints.

- RTC will utilize the AS Offer structure that will be in place with the implementation of Nodal Protocol Revision Request (NPRR) 863.

- The AS Offer submission window will be consistent with the Energy Offer Curve (EOC) submission window.

- Proxy AS Offers will be created for Resources that do not have a valid AS offer curve for the entire operating range of the Resource for use in the Real-Time Market (RTM) will be consistent with the following guidelines:

  - The proxy offer will be a linked AS Offer across all AS products for which a Resource is qualified to provide. For Generation Resources, the proxy offer MW will be HSL.

  - For each AS where the Resource has a submitted AS Offer, the price in the proxy AS Offer for that AS will be set equal to the maximum of the Resource’s highest offer price for that AS up to the HSL of the Resource.

- For each AS where the Resource has not submitted an AS Offer, the price in the proxy AS Offer for that AS up to the HSL of the Resource will be set equal to zero  {Note that the IMM in filed initial comments before the PUC in Project 48540 question 9, states:

“Withholding should not be allowed. Much like Resources are required to offer their full capacity for energy production when On-Line, resources should be required to offer their full AS-qualified capacity while online. Under current market design, if a Resource does not submit an energy offer for the entire amount of available capacity, ERCOT systems generate a 'proxy energy offer on behalf of the Resource. The price assumed for any such proxy energy offer is the highest price contained in the Resource submitted offer. In contrast, the IMM recommends that the default offer for any qualified AS capacity that is not actively priced should be $0/MWh because Resources available to offer energy in Real-Time are generally able to offer AS at no additional cost. If circumstances arise that preclude the availability of particular AS while a Resource is On-Line, the Resource should be required to submit either an Outage or change of status reflecting that limitation”.

The IMM further reiterated this in its Reply Comments in the same project question 9, A. Prohibitions on Withholding; stating:

“… In contrast, the IMM recommends that the default offer for any qualified and available AS capacity that is not actively priced should be $0/MWh under the presumption that the marginal cost of providing AS from online, AS-available, AS-qualified capacity is zero.”}.

- The system will be designed to allow different proxy price floors for instances in which the same AS can be provided by either Off-Line or On-Line Resources (i.e., the proxy price floor for an offline Non-Spin offer may be different than the proxy price floor for an online Non-Spin offer).

- The RTC optimization will enforce various Resource specific AS constraints to ensure the AS awards are feasible, considering both QSE submitted AS offers and RTC created proxy AS Offers.

- Proxy AS Offers will not be created for Resources for use in the DAM.

# Future Decision Points and Issues for Developing Principle Concepts

- Additional concepts related to constraint formulation (e.g., treatment of Resources with an ONRR status)

- Potential changes to Verifiable Costs

- Creation of AS Offer floors

- Changes to validation of AS trades (related to AS self-provision in Real-Time)

| Applicable Protocol Section(s) |  |
| --- | --- |
| Impacted System(s) / Application(s) |  |

# Appendix Material with additional details

- QSEs will have the ability in Real-Time to indicate whether a Resource is temporarily unable to provide AS due to operational constraints.

Details under development:

- For scenarios where the reduced AS capability is less than the QSE-submitted AS Offer (MW), QSEs can, via Resource-specific telemetry, inform ERCOT of the reduced AS capability (MW) by specific AS type from a Resource. {I am not sure this will be the best way of doing this, as it can lead to issues where the total reserve on a Resource is more or less than the amounts from telemetry of AS values.  This is the classic problem of having two wrist watches -- you do not know what time it is.  Seems to me a better method may be for ERCOT to calculate the amounts of AS that could be available by starting with the HSL minus the current Resource MW.  Then ERCOT would allocate the total reserves on a Resource first to Reg-up, then Responsive, etc., using information for which the Resource is qualified.  If a QSE has a temporary problem with a particular AS, then a status indicator to ERCOT via telemetry would suffice. Using a method like this assures that all the capability a Resource has will be used in RTC, even when a QSE changes its HSL or moves its actual generation through normal operation of a unit.  I think this need to be discussed further.}

- Under RTC, ERCOT systems will use Resource-specific telemetered values to limit AS awards.  See above comments

- ERCOT will be proposing to add new Resource-specific telemetry points (analog – MW) for each AS type/subtype:

  - Regulation Up (Reg-Up) capability;

  - Regulation Down (Reg-Down) capability;

  - Fast Responding Regulation Up Service (FFRS-Up) capability;

  - Fast Responding Regulation Down Service (FFRS-Down) capability;

  - RRS PFR capability;

  - RRS UFR capability;

  - RRS FFR capability;

  - ECRS capability; and

  - Non-Spinning Reserve (Non-Spin) capability.

- Future discussion will also address whether a QSE with a submitted telemetered Ramp Rate up for a Resource with a High Dispatch Limit (HDL) that is greater than the Resource’s telemetered MW, should be able to indicate that the Resource is unable to provide Reg-Up, ECRS and/or Non-Spin.

- UFR Load Resources will be able to self-provide RRS UFR and ECRS; the amount of which will based on DAM awards and AS trades.  (see above comment)

- MOCs for On-Line hydro Generation Resources not operating in ONRR mode shall allow for RRS, Non-Spin, and ECRS to be maintained on those Resources.

Details under development:

- Under RTC, UFR Load Resources will not be capable of arming and disarming UFR relays based on non-zero/zero AS awards if treated like Generation Resources

  - New Resource-specific telemetry points (analog – MW) will be added for RRS UFR, RRS FFR and ECRS, allowing ERCOT visibility into MW service quantities self-provided by a UFR Load Resource. {Is this telemetry “new” given that it should be required today?}

    - System-wide RRS and ECRS AS Demand Curves (ASDCs) will be reduced by the validated amount of UFR Load Resource self-provided service quantities.

    - ERCOT is in the process of developing validation processes and rules regarding these new telemetry values.

      - The 60% limitation rule (per NPRR 863) for system-wide RRS from UFR Load Resources and FFR and the annually determined limit from FFR will be maintained.

      - Telemetered UFR Load Resource self-provided RRS, ECRS MW amounts with respect to DAM awards and AS Trades under normal conditions and scarcity conditions will be reconciled.

- Under RTC, On-Line hydro Generation Resources not operating in ONRR mode must adhere to constraints imposed by governmental agencies or by treaty regarding the operations of those Resources.  These Resources often have the opportunity to provide incremental energy in response to a deployment of AS and are therefore good candidates to provide AS, but cannot regularly exchange the AS capacity for an incremental energy deployment.  The MOC for On-Line hydro Generation Resources shall be set equal to the submitted Energy Offer Curve.

- RTC will account for will account for frequency responsive capacity of a CCGR when awarding Regulation and RRS PFR.

Details under development:

- An On-Line CCGR can have portions of its capacity that are not frequency responsive (e.g., steam generator, duct burner, etc.).  Therefore, under RTC, Real-Time results should not be such that awarded Regulation and/or RR PFR (or portions thereof) could be coming from CCGR capacity that is Non-Frequency Responsive Capacity (NFRC).

- ERCOT will be proposing an enhanced mathematical model of CCGR, and new telemetry to account for frequency responsive capacity of a CCGR for awarding Regulation and RRS PFR.

- The settlements that were previously discussed for manually deployed Responsive on UFR Resources seem to be making a big change in the way these Resources are currently settled. Many Load Resources are represented by a REP who may or may not pass back to the individual LR any funds for that Resource’s interruption due to manual deployment.  We should consider, when these Resources are manually interrupted, that the total amout of Responsive is reduced since, when these Resources change status to off, the amount of PRC on generation is increased by a like amount. During the time these Resources are off due to manual deployment, the system total Responsive needed should be reduced by the amount of MW deployed.

Many UFR providers are under long term contracts with REPs.  At the time RTC is actually implemented (highly variable), the contracts may not recognize any settlements differently

than they do today. It might be cleaner if RTC TF adopted a “Principle” that LRs on UFR will not incur more market risks than they currently have in today’s market.