| NPRR Number | 919 | NPRR Title | Exemption from Governor Primary Frequency Response Control for Certain Resources in Private Use Networks |
| --- | --- | --- | --- |
| Date of Decision |  | September 12, 2019 |  |
| Action |  | Rejected |  |
| Timeline |  | Normal |  |
| Proposed Effective Date |  | Not applicable |  |
| Priority and Rank Assigned |  | Not applicable |  |
| Nodal Protocol Sections Requiring Revision |  | 8.5.1.1, Governor in Service |  |
| Related Documents Requiring Revision/Related Revision Requests |  | NOGRR184, Related to NPRR919, Exemption from Governor Primary Frequency Response Control for Certain Resources in Private Use Networks |  |
| Revision Description |  | This Nodal Protocol Revision Request (NPRR) allows a Resource in a Private Use Network whose primary function is providing steam to a host, and is not participating in the ERCOT energy market, to be exempted from Primary Frequency Response service requirements. The Governor will still be in service, but may be allowed to be in pressure control instead of Primary Frequency Response control. |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |  |
| Business Case |  | The intent of this exclusion is to reduce or eliminate unnecessary Primary Frequency Response model validation testing per North American Electric Reliability Corporation (NERC) Standard MOD-027-1, Verification of Models and Data for Turbine/Governor and Load Control or Active Power/Frequency Controls Functions; and Primary Frequency Response testing per Section 8.5.1.1 and paragraph (2) of Nodal Operating Guide Section 2.2.7, Turbine Speed Governors. |  |
| Credit Work Group Review |  | Not applicable |  |
| PRS Decision |  | On 2/14/19, PRS unanimously voted to table NPRR919 and refer the issue to ROS. All Market Segments were present for the vote. On 9/12/19, PRS unanimously voted to reject NPRR919. All Market Segments were present for the vote. |  |
| Summary of PRS Discussion |  | On 2/14/19, there was no discussion. On 9/12/19, participants reviewed the 9/6/19 ROS comments to NPRR919. |  |

| Sponsor |  |
| --- | --- |
| Name | Eric Woelfel |
| E-mail Address | ewoelfel@fpcusa.com |
| Company | Formosa Utility Venture, Ltd. |
| Phone Number | 973-716-7389 |
| Cell Number | 973-634-6107 |
| Market Segment | Independent Generator |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Phillip Bracy |
| E-Mail Address | Phillip.Bracy@ercot.com |
| Phone Number | 512-248-6917 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| ROS 030819 | Requested PRS table NPRR919 to allow for review by the Performance Disturbance Compliance Working Group (PDCWG) |
| Formosa 032219 | Modified language to further restrict proposed exemption exclusively to simple cycle steam turbine Generation Resources |
| ERCOT 062819 | Opposed general concept of creating exemptions for certain resources/Market Participants from reliability obligations in Protocols; proposed alternative revisions as a compromise solution in the case that Market Participants deem the exemption to be appropriate |
| ROS 090619 | Requested PRS reject NPRR919 |

Market Rules Notes

Please note that the baseline language in the following sections has been updated to reflect the incorporation of the following NPRRs into the Protocols:

- NPRR863, Creation of ERCOT Contingency Reserve Service and Revisions to Responsive Reserve (incorporated 3/1/19)

  - Section 8.5.1.1

- NPRR921, RTF-2 Elimination of the Terms All-Inclusive Generation Resource and All-Inclusive Resource (incorporated 7/1/19)

  - Section 8.5.1.1

Please note that administrative revisions have been made to the language and authored as “ERCOT Market Rules”.

Proposed Protocol Language Revision

8.5.1	Generation Resource and QSE Participation

8.5.1.1	Governor in Service

(1)	At all times an All-Inclusive Generation Resource is On-Line, its Governor must remain in service and be allowed to respond to all changes in system frequency except during startup, shutdown, or testing.  A Generation Entity may not reduce Primary Frequency Response on an individual All-Inclusive Generation Resource even during abnormal conditions without ERCOT’s consent (conveyed by way of the Resource Entity’s Qualified Scheduling Entity (QSE)) unless equipment damage is imminent.  All All-Inclusive Generation Resources that have capacity available to either increase output or decrease output in Real-Time must provide Primary Frequency Response, which may make use of that available capacity.  Only Generation Resources providing Regulation Up (Reg-Up), Regulation Down (Reg-Down), Responsive Reserve (RRS), or Non-Spinning Reserve (Non-Spin) from On-Line Resources, as specified in Section 8.1.1, QSE Ancillary Service Performance Standards, shall be required to reserve capacity that may also be used to provide Primary Frequency Response.

[NPRR863 and NPRR921: Replace applicable portions of paragraph (1) above with the following upon system implementation of NPRR863 or NPRR889, respectively:] (1) At all times a Generation Resource, Settlement Only Transmission Generator (SOTG), or Settlement Only Transmission Self-Generator (SOTSG) is On-Line, its Governor must remain in service and be allowed to respond to all changes in system frequency except during startup, shutdown, or testing. A Generation Entity may not reduce Primary Frequency Response on an individual Generation Resource or Settlement Only Generator (SOG) even during abnormal conditions without ERCOT’s consent (conveyed by way of the Resource Entity’s Qualified Scheduling Entity (QSE)) unless equipment damage is imminent. All Generation Resources, SOTGs, and SOTSGs that have capacity available to either increase output or decrease output in Real-Time must provide Primary Frequency Response, which may make use of that available capacity. Only Generation Resources providing Responsive Reserve (RRS), Regulation Up (Reg-Up), Regulation Down (Reg-Down), ERCOT Contingency Reserve Service (ECRS), or Non-Spinning Reserve (Non-Spin) from On-Line Resources, as specified in Section 8.1.1, QSE Ancillary Service Performance Standards, shall be required to reserve capacity that may also be used to provide Primary Frequency Response.

[NPRR863 and NPRR921: Insert applicable portions of paragraph (2) below upon system implementation of NPRR863 or NPRR889, respectively:] (2) Generation Resources, SOTGs, and SOTSGs that do not have an RRS or Regulation Service Ancillary Service Resource Responsibility shall set their Governor Dead-Band no greater than ±0.036 Hz from nominal frequency of 60 Hz. A Generation Resource, SOTG, or SOTSG that widens its Governor Dead-Band greater than what is prescribed in Nodal Operating Guide Section 2.2.7, Turbine Speed Governors, must update its Resource Registration data with the new dead-band value.

(3)	At ERCOT’s sole discretion, any Generation Resource in a Private Use Network that is solely used for providing steam and has a zero High Sustained Limit (HSL) for at least 24 months may be granted an exemption from having the Governor in Primary Frequency Response service.  The Governor may instead have the option of being in pressure control service.  This specific Generation Resource would also not be permitted to participate in any ancillary service market.  The requesting Generation Resource should submit to ERCOT an attestation and supporting evidence showing the HSL for the requesting Generation Resource was zero for at least 24 months.  ERCOT shall make a determination on the exemption within 60 days of receipt of the attestation.