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[bookmark: _Toc181432029][bookmark: _Toc221086140][bookmark: _Toc257809882][bookmark: _Toc307384191][bookmark: _Toc532803590][bookmark: _Toc12525371]5.7.1	Generation Resource Data Requirements
(1)	The Interconnecting Entity (IE) shall submit with its Generation Interconnection or Change Request (GINR) the most current actual facility information (generation, substation, and transmission/subtransmission if applicable) or best available expected performance data for the physical and electrical characteristics of all proposed facilities (in sufficient detail to provide a basis for modeling) up to the Point of Interconnection (POI) with a Transmission Service Provider (TSP).  
(2)	Failure to supply the required data may delay ERCOT processing of the interconnection application and studies.  Recommendations resulting from these studies that are based on outdated, false, or bad data may adversely affect the safety and reliability of the ERCOT System and can result in damage to generation or transmission equipment.  The IE and subsequently, the Resource Entity associated with any approved Generation Resource, must promptly submit any updates to ERCOT to ensure the long-term adequacy, reliability, and safety of the ERCOT System, as required by the Protocols, this Planning Guide, the Operating Guides, and North American Electric Reliability Corporation (NERC) Reliability Standards.  Failure to comply may result in financial penalties.
(3)	In an effort to produce the best available Security Screening Study and Full Interconnection Study (FIS), ERCOT suggests that IEs begin collecting all appropriate engineering and equipment data from manufacturers as soon as the IE selects its major equipment for the proposed project.
(4)	While the duty to update data may require additional information, at a minimum, the IE shall submit the following data via the online Resource Integration and Ongoing Operations (RIOO) system at each step of the process:
(a)	Application and Security Screening Study:
(i)	Generation Entity Information Sheet; and
(ii)	Generation Interconnection Screening Study Request Data.
(b)	FIS:
(i)	Updates to the above information (if necessary);
(ii)	Applicable data required for interconnection studies as defined in the Resource Registration Glossary applicable to the Generation Resource type;
(iii)	Provision of the appropriate dynamic model for the proposed Generation Resource and results of model quality tests and associated simulation files as described in paragraph (5)(b) of Planning Guide Section 6.2, subject to performance and usability verification by the lead TSP with approval from ERCOT(some standard dynamic model forms are posted on the ERCOT website);
(iv)	Dynamic model data shall be provided utilizing the appropriate dynamic model templateIf alternative models are required to appropriately represent the proposed Generation Resource, an alternative model may be provided by the IE, subject to verification by the lead TSP and ERCOT; and
(v)	In order to perform stability (transient and voltage) analyses, the IE shall provide unit dynamicstability model information and data to the TSP(s) and ERCOT via the online RIOO system.  Section 6.2 (5), Dynamic Model Development, and Tthe Dynamics Working Group Procedureal Manual contains more detail and IE dynamics data requirements.  Data submitted for transient stability models shall be compatible with ERCOT standard models (Siemens/PTI PSS/E and Powertech Labs Inc TSAT, VSAT and SSAT).  If no compatible model exists, the IE shall work with a consultant or software vendor to develop and supply accurate/appropriate models along with other associated data.  These models shall be incorporated into the standard model libraries of both software packages.  It is recommended that generation owners and developers encourage manufacturers and software vendors to work together to develop and maintain these important models.
[bookmark: _Toc257809886][bookmark: _Toc257809885](c)	Prior to start of construction:
(i)	Any significant design changes in the generator(s) or main power transformer(s) of the proposed Generation Resource shall be provided to ERCOT and the TSP to ensure compatibility with the existing transmission system.
 (d)	Prior to the Resource Commissioning Date:
(i)	Registration and official Resource Registration data submittal pursuant to Section 6.8.2, Resource Registration Process;
(ii)	Updates to Resource Registration data based on “as-built” or “as-tested” data in all cases; and 
(iii)	Proof of meeting ERCOT requirements (reactive, low Voltage Ride-Through (VRT) standards, dynamicstability models, Power System Stabilizer (PSS), Subsynchronous Resonance (SSR) models).
[bookmark: _Toc257809887](e)	During continuing operations:
(i)	The IE shall provide ERCOT and the TSP with any equipment data changes which result from equipment replacement, repair, or adjustment.  Unless otherwise required in the Protocols, this Planning Guide or the Operating Guides, the IE shall provide such data to ERCOT and the TSP no later than 60 days prior to the date of the actual change in equipment characteristics or during annual data update filings whichever occurs first.  This requirement shall also apply to all future owners throughout the service life of the project/plant.
	[PGRR066 and PGRR069:  Replace applicable portions of Section 5.7.1 above with the following upon system implementation of PGRR066 or NPRR921:]
[bookmark: _Toc532809403][bookmark: _Toc12525372]5.7.1	Generation Resource and Settlement Only Generator Data Requirements
(1)	The Interconnecting Entity (IE) shall submit with its Generation Interconnection or Change Request (GINR) the most current actual facility information (generation, substation, and transmission/subtransmission if applicable) or best available expected performance data for the physical and electrical characteristics of all proposed facilities (in sufficient detail to provide a basis for modeling) up to the Point of Interconnection (POI) with a Transmission Service Provider (TSP).  
(2)	Failure to supply the required data may delay ERCOT processing of the interconnection application and studies and result in a GINR cancellation as described in Section 5.7.7, Cancellation of a Project Due to Failure to Comply with Planning Guide Requirements.  Recommendations resulting from these studies that are based on outdated, false, or bad data may adversely affect the safety and reliability of the ERCOT System and can result in damage to generation or transmission equipment.  The IE and subsequently, the Resource Entity associated with any approved Generation Resource or Settlement Only Generator (SOG), must promptly submit any updates to ERCOT to ensure the long-term adequacy, reliability, and safety of the ERCOT System, as required by the Protocols, this Planning Guide, the Operating Guides, and North American Electric Reliability Corporation (NERC) Reliability Standards.  Failure to comply may result in financial penalties.
(3)	In an effort to produce the best available Security Screening Study and Full Interconnection Study (FIS), ERCOT suggests that IEs begin collecting all appropriate engineering and equipment data from manufacturers as soon as the IE selects its major equipment for the proposed project.
(4)	While the duty to update data may require additional information, at a minimum, the IE shall submit the following data via the online Resource Integration and Ongoing Operations (RIOO) system at each step of the process:
(a)	Application and Security Screening Study:
(i)	Generation Entity Information Sheet; and
(ii)	Generation Interconnection Screening Study Request Data.
(b)	FIS:
(i)	Updates to the above information (if necessary);
(ii)	Applicable data required for interconnection studies as defined in the Resource Registration Glossary applicable to the resource type;
(iii)	Provision of the appropriate dynamic model for the proposed Generation Resource or SOG and results of model quality tests and associated simulation files as described in paragraph (5)(b) of Planning Guide Section 6.2, subject to performance and usability verification by the lead TSP with approval from ERCOT(some standard dynamic model forms are posted on the ERCOT website);
(iv)	Dynamic model data shall be provided utilizing the appropriate dynamic model templateIf alternative models are required to appropriately represent the proposed Generation Resource or SOG, an alternative model may be provided by the IE, subject to verification by the lead TSP and ERCOT; and
(v)	In order to perform stability (transient and voltage) analyses, the IE shall provide unit dynamicstability model information and data to the TSP(s) and ERCOT via the online RIOO system.  Section 6.2 (5), Dynamic Model Development and Tthe Dynamics Working Group Procedureal Manual contains more detail and IE dynamics data requirements.  Data submitted for transient stability models shall be compatible with ERCOT standard models (Siemens/PTI PSS/E and Powertech Labs Inc TSAT, VSAT and SSAT).  If no compatible model exists, the IE shall work with a consultant or software vendor to develop and supply accurate/appropriate models along with other associated data.  These models shall be incorporated into the standard model libraries of both software packages.  It is recommended that generation owners and developers encourage manufacturers and software vendors to work together to develop and maintain these important models.
 (c)	Prior to start of construction:
(i)	Any significant design changes in the generator(s) or main power transformer(s) of the proposed Generation Resource or SOG shall be provided to ERCOT and the TSP to ensure compatibility with the existing transmission system.
 (d)	Prior to the Resource Commissioning Date:
(i)	Registration and official Resource Registration data submittal pursuant to Section 6.8.2, Resource Registration Process;
(ii)	Updates to Resource Registration data based on “as-built” or “as-tested” data in all cases; and 
(iii)	Proof of meeting ERCOT requirements (reactive, low Voltage Ride-Through (VRT) standards, dynamicstability models, Power System Stabilizer (PSS), Subsynchronous Resonance (SSR) models).
(e)	During continuing operations:
(i)	The IE shall provide ERCOT and the TSP with any equipment data changes which result from equipment replacement, repair, or adjustment.  Unless otherwise required in the Protocols, this Planning Guide or the Operating Guides, the IE shall provide such data to ERCOT and the TSP no later than 60 days prior to the date of the actual change in equipment characteristics or during annual data update filings whichever occurs first.  This requirement shall also apply to all future owners throughout the service life of the project/plant.



[bookmark: _Toc283904714][bookmark: _Toc533168263]6.2	Dynamics Model Development
(1)	To adequately simulate dynamic and transient events in the ERCOT System, it is necessary to establish and maintain dynamics data and simulation-ready study cases representing the dynamic capability and frequency characteristics of machines and equipment connected to the ERCOT System.
(2)	Dynamics data is the network data and mathematical models required in accordance with the Reliability and Operations Subcommittee (ROS)-approved Dynamics Working Group Procedureal Manual for simulation of dynamic and transient events in the ERCOT System. 
(3)	For Resource Entities, dynamics data includes the data needed to represent the dynamic and transient response of Resource Entity-owned devices and/or Loads including but not limited to generating units, plants, and other equipment when connected to the ERCOT System including the data for any privately owned transmission system or collection system used to connect the Resource to the ERCOT System.
(4)	For Transmission Service Providers (TSPs), dynamics data needed to represent the dynamic and transient capability of TSP-owned devices including but not limited to Load shedding relays, protective relays, FACTS devices (e.g., DVARS, SVC, STATCOM, SMES), Direct Current Ties (DC Ties), variable-frequency transformers, automatically switched shunts, and transformers with automatic load tap changers.  
(5)	All dynamics data must be compatible with the current version of the planning model software as described in the Dynamics Working Group Procedural Manual. 
(6)	The Facility owner shall provide appropriate dynamics data to ERCOT and the interconnecting TSP including the data for a planned Facility. The dynamic data shall include the following:
(a) A model with parameters that accurately represent the dynamics of the device and that is compatible with the current version of the planning and operations model software as described in the Dynamics Working Group Procedure Manual.  If a user written model is provided, the data shall also include the following:
(i) The Dynamic Linked Library (DLL) file – the user written model must be provided in DLL format;
(ii) A technical description of the model characteristics including detailed control block diagrams, design logic, and descriptions for all model parameters and variables;
(iii) A user manual to describe procedures and considerations for using the model in dynamic simulations including steady state representation and limitations for model adequacy and usability in the software.  The model shall allow the user to determine the allocation of the bus number and machine IDs without restriction.
(b) Results of model quality tests and associated simulation files that demonstrate acceptable performance of the models in the software as described in the Dynamics Working Group Procedure Manual.  The purpose of these tests is to ensure the quality of the provided dynamic data and models for use in numerous system studies.  Therefore, the facility owner should also assess sufficient sensitivities, including but not limited to voltage set point at POI, real power output, and reactive power output to ensure acceptable model performance over the entire range of operating conditions.
(i) All site-specific dynamic models required to represent the Facility shall be included in the model quality tests.  These tests can be performed in a simple test system without requiring the ERCOT grid information.
(ii) The dynamic model shall represent the aggregate Generator Resource as set forth in paragraph (12) of Protocol Section 3.10.7.2, Modeling of Resources and Transmission Loads.
(iii) Results for the following model quality tests shall be provided to demonstrate acceptable model performance.  Additional details about each test, including the set up and description of desirable response, are included in the Dynamics Working Group Procedure Manual.  
(a) Flat start test: A no-disturbance test shall be performed to demonstrate appropriate model initialization and the Facility’s dynamic response under a no-disturbance condition. 
(b) Small voltage disturbance test: A voltage step increase and decrease shall be applied to the POI to demonstrate the Facility’s dynamic response.
(c) Large voltage disturbance test:
(i) For IRR and inverter-based Resources, the high and low voltage ride through profiles as described in Nodal Operating Guides, Section 2.9.1 shall be applied to the POI to demonstrate the Facility’s dynamic response.
(ii) For a non-IRR Resource, a fault shall be applied to the POI to demonstrate the Facility’s dynamic response.
(d) Small frequency disturbance test: A frequency step increase and decrease shall be applied to the POI to demonstrate the Facility’s dynamic response.  
(e) System strength test: The model for IRR and inverter-based Resources shall be tested under a few equivalent short circuit ratios, as described in the Dynamics Working Group Procedural Manual.  This tests the robustness of the model to varying system conditions. 
(67)	Dynamics data for a planned Facility will be updated by the Facility owner upon completion of the design for the Facility.
(78)	Updated dynamics data for an existing Facility shall be provided to ERCOT when field tests, inspections, or other information demonstrates that the dynamics data should be changed to accurately represent the dynamic characteristics of the Facility.
(89)	Dynamics Data is considered Protected Information pursuant to Protocol Section 1.3, Confidentiality.
(910)	Dynamics data shall be provided with the legal authority to provide the information to all TSPs.  If any of the information is considered Protected Information, the Facility owner shall indicate as such.
[bookmark: _Toc248276885][bookmark: _Toc533168264]6.2.1	Dynamics Data Requirements for Resources
[bookmark: _Toc147762164][bookmark: _Toc147762503][bookmark: _Toc147762596][bookmark: _Toc147886698][bookmark: _Toc147886740](1)	A Resource Entity shall submit new or updated dynamics data in accordance with Section 5, Generation Resource Interconnection or Change Request.  The Resource Entity shall provide all dynamics data as described in Section 6.2 (5) and the Dynamics Working Group Procedureal Manual.  The Resource Entity shall provide an accurate and appropriate model and model parameters.  Resource Entities are encouraged to use standard models to represent the Resource’s dynamic and transient capability and response.  If no appropriate standard model is available, the Resource Entity shall submit a model, model documentation, and the associated model parameters to ERCOT for inclusion in simulation-ready study cases as described in the Dynamics Working Group Procedural Manual.
(2)	A Resource Entity is responsible for tuning and validating the parameters that go into their models to ensure that the models produce an accurate representation of a device’s capability and response.  If ERCOT, the interconnecting TSP, or the Dynamics Working Group (DWG) identifies inappropriate or incomplete dynamics data, ERCOT, in its sole discretion, may reject the submitted dynamic data and will provide the Facility Owner an explanation for the rejection.  The Resource Entity shall take action to resolve discrepancies  and provide updated dynamic data to ERCOT and the interconnecting TSP within 30 days. with the Resource Entity.
[bookmark: _Toc533168265]6.2.2	Dynamics Data Requirements for Load Resources
(1)	ERCOT shall provide the updated Load Resource relay models.
(2)	Load Resource relay models shall be updated as describe in the Dynamics Working Group Procedureal Manual.
[bookmark: _Toc248276888][bookmark: _Toc533168266]6.2.3	Dynamics Data Requirements for Transmission and/or Distribution Service Providers
(1)	The owner of under-frequency Load shedding equipment shall provide necessary data to model under frequency Load shedding relays for their portion of the ERCOT System as described in the Dynamics Working Group Procedure Manual.
(2)	The owner of under voltage Load shedding equipment shall provide necessary data to model under voltage Load shedding relays for their portion of the ERCOT System as described in the Dynamics Working Group Procedure Manual.
(3)	When requested by ERCOT or a Transmission and/or Distribution Service Provider (TDSP), the owner of protective relays, control systems, and Remedial Action Schemes (RASs) shall provide dynamics data needed to simulate their action.
(4)	The DWG shall document appropriate Load model data as described in the Dynamics Working Group Procedure Manual for use in dynamic simulations.
(5)	The owner of a dynamic element connected to the transmission system shall provide the dynamic data needed to simulate the action of the device in dynamic simulations to ERCOT and the TDSP to which the element is connected.  
[bookmark: _Hlk494805952](6)	The owner of a dynamic element connected to the transmission system shall verify the dynamic models through comparison with operational data of actual events or test results within five years of energization and a minimum of every ten years thereafter.  Industry accepted testing techniques shall be used for testing, measuring and calculating the modeling parameters.  The owner of the dynamic element shall document and retain results for the model verification effort.  Documentation shall include the operational data used to verify the modeling parameters. 
[bookmark: _Toc533168267]6.2.4 	Dynamics Data Screening and Maintenance 
(1)	In order to maintain simulation-ready base cases and associated dynamics data files for use in dynamic simulations, ERCOT, in consultation with the DWG, shall perform dynamic simulations called flat-start simulations as described in the Dynamics Working Group Procedureal Manual.
(2)	The schedule for producing the flat start simulations will be reviewed annually and submitted to the ROS.
(3)	Transmission owners shall review the completeness and applicability of dynamics data used in the flat start simulation for equipment connected to their system.  The model should be appropriate for the equipment and the data shall be appropriate for the model.
(4)	ERCOT shall contact the appropriate TSP or Resource Entity to resolve any dynamics data problems, incomplete or missing data, encountered while preparing the flat start simulation.
(5)	Upon completion of each flat start simulation, ERCOT shall distribute an electronic copy of all files necessary to replicate the flat start simulation as described in the Dynamics Working Group Procedureal Manual to the DWG.
(6)	ERCOT and the DWG shall document assumptions made, data created, and data changed during the creation of a flat start simulation.  
(7)	ERCOT shall be responsible for storing all of the dynamics data and shall maintain a repository of dynamics data with tuned parameters and any submitted revisions.  
(8)	Within 30 days of receipt, ERCOT shall forward all dynamics data received to the TSP to which the dynamics device is connected.
[bookmark: _Toc533168268]6.2.5 	Dynamics Data Recorder
(1)	ERCOT, in consultation with the DWG, shall prepare a list of locations, based on criteria contained in the Dynamics Working Group Procedureal Manual, which require the installation of devices capable of recording ERCOT Transmission Grid events with sufficient resolution to serve as a benchmark for dynamic simulations.
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