| NOGRR Number | 191 | NOGRR Title | Related to NPRR939, Modification to Load Resources Providing RRS to Maintain Minimum PRC on Generators During Scarcity Conditions |
| --- | --- | --- | --- |

| Date | September 26, 2019 |
| --- | --- |

| Submitter’s Information |  |
| --- | --- |
| Name | Ann Boren |
| E-mail Address | ann.boren@ercot.com |
| Company | ERCOT |
| Phone Number | 512-275-6465 |
| Market Segment | Not applicable |

Comments

ERCOT submits these comments in order to align proposed language in Nodal Operating Guide Revision Request (NOGRR) 191 with the incorporation of NOGRR187, Related to NPRR863, Creation of ERCOT Contingency Reserve Service and Revisions to Responsive Reserve, into the Nodal Operating Guide.

Revised Cover Page Language

None

Revised Proposed Guide Language

- 4.8.1	Responsive Reserve Service Manual Deployment

(1)	RRS for capacity may be manually deployed (HASL released) when the system approaches scarcity conditions so that the capacity reserved behind HASL will be released to Security-Constrained Economic Dispatch (SCED).

(a)	When HASL – (Gen + 5 minute load ramp) <= 200 MW, ERCOT may deploy the available RRS capacity from Generation Resources and Controllable Load Resources in 500 MW increments after all the available Non-Spinning Reserve (Non-Spin) service has been deployed and Resources have responded to any earlier deployments.

(b)	When HSL – (Gen + 5 minute load ramp) <= 500 MW, ERCOT may deploy Load Resources controlled by high-set under-frequency relays providing RRS.

[NOGRR187: Replace paragraph (1) above with the following upon system implementation of NPRR863:] (1) RRS for capacity may be manually deployed (HASL released) when the system approaches scarcity conditions so that the capacity reserved behind HASL will be released to SCED. (a) When HASL – (Gen + 5 minute load ramp) <= 200 MW, ERCOT may deploy the available RRS capacity from Generation Resources and Controllable Load Resources in 500 MW increments after all the available ECRS (dispatchable by SCED) and Non-Spinning Reserve (Non-Spin) service has been deployed and Resources have not responded to any earlier deployments. (b) When HSL – (Gen + 5 minute load ramp) <= 500 MW, ERCOT may deploy Load Resources controlled by high-set under-frequency relays providing RRS.