| Date: | October 1, 2019 |
| --- | --- |
| To: | Board of Directors |
| From: | Bob Helton, Technical Advisory Committee (TAC) Chair |
| Subject: | Application for Permanent Site-Specific Exemption from Compliance with Paragraph (6) of Protocol Section 10.3.2.3, Generation Netting for ERCOT-Polled Settlement Meters (Air Liquide Large Industries U.S. LP) |

## Issue for the ERCOT Board of Directors

ERCOT Board of Directors Meeting Date: October 8, 2019 Item No.: 2.2

##### Issue: Whether the ERCOT Board of Directors (Board) should approve Air Liquide Large Industries U.S. LP’s (Air Liquide’s) application for permanent site-specific exemption from compliance with paragraph (6) of Protocol Section 10.3.2.3.

##### Background/History: Paragraph (6) of Protocol Section 10.3.2.3 provides: (6) For purposes of this Section, a common switchyard is defined as an electric substation Facility where the POI for Load and Generation Resources are located at the same Facility but where the interconnection points are physically not greater than 400 yards apart. The physical connections of the Load to its POI and the Generation Resource to its POI cannot be Facilities that have been placed in a TSP’s or DSP’s rate base. On 9/25/19, TAC unanimously approved Air Liquide’s application for a permanent exemption under the provisions of and in accordance with the information and data requirements found in Protocol Section 10.14.3.1, Information to be Included in the Application. Each of the requirements and a summary of the associated portions of the application are as follows: The application for exemption to ERCOT shall include: (a) A detailed description of the exemption sought. including specific reference to the relevant Section(s) of these Protocols or the SMOG authorizing ERCOT to grant the exemption, and the Metering Facilities to which the exemption will apply; Air Liquide seeks approval by TAC and the Board for a permanent exemption from the requirements in paragraph (6) of Protocol Section 10.3.2.3 for the Bayou-Bayport Complex, including all six ERCOT-Polled Settlement (EPS) Meters at the site as shown on EPS Metering Design Proposal, TDSP Project Number 100-BYU, Meter IDs: BYU_G1, BYU_G2, BYU_G3, BYU_G4, Choate_Plant, BBP_Plant. (b) A detailed statement of the reason for seeking the exemption, including any supporting documentation; The Bayou-Bayport Complex (Complex) in Harris County, Texas is wholly owned by Air Liquide. The Complex is a vital component of Air Liquide’s Texas Gulf Coast operations and supply network. The Complex has supplied oxygen, nitrogen, argon, hydrogen, steam, and water to customers for over 50 years, before ERCOT served as the central operating coordinator for Texas, and prior to ERCOT functioning as a single control area in 2001. The original interconnection configuration for the Complex also predates the competitive market, and was designed in coordination with CenterPoint’s vertically integrated predecessor, Houston Lighting & Power (HL&P). The netting arrangement at the Complex was initially approved by ERCOT’s metering department on May 17, 2001, permitting netting of generation and auxiliary loads supporting the generation. In 2002, the meter design was amended to add non-auxiliary load from Air Liquide and new metering points, and an additional amendment was approved in May 2005 to add another meter. The netting arrangement in place today has been subsequently reapproved several times in conjunction with updates to the meter design, most recently in 2015. The intent of Protocol Section 10.3.2.3 was to allow certain interconnections that predated the competitive market, such as the Bayou-Bayport Complex, to continue to receive the same treatment previously applied by the bundled utilities (in this case, HL&P). Protocol Section 10.3.2.3 allows net metering for a facility with multiple Points of Interconnection (POIs) where: (1) “the Loads and generator output are electrically connected to a common switchyard,” meaning in part that the interconnection points “are physically not greater than 400 yards apart”; and (2) there is “sufficient generator capacity to serve all plant Loads for netting to occur.” The Protocols do not explicitly describe how the 400-yard distance should be measured under Section 10.3.2.3 with respect to certain equipment and configurations that may exist at the POIs; in particular, the relevant interconnection points within a substation are not explicitly defined. As a result, Air Liquide and CenterPoint Energy Inc. have historically used a measurement convention that is slightly different from what ERCOT uses during a site audit. Air Liquide was unaware of this discrepancy until it was identified through a recent metering site audit and subsequent discussions with ERCOT. Air Liquide views both measurement approaches as reasonable, and maintains that all prior metering design approvals and net metering treatment for the Complex remain legally valid. However, Air Liquide seeks this permanent exemption to align the historical treatment of the Bayou-Bayport Complex with ERCOT’s measurement practices. (c) Details of the Entity(s) to which the exemption will apply; The exemption will apply to Air Liquide Large Industries U.S. LP, as the registered Resource Entity for the Bayou-Bayport Complex. (d) Details of the location to which the exemption will apply; This exemption will apply to the Bayou-Bayport Complex located at 11777 Bay Area Boulevard in Pasadena, Texas, 77507 and includes all six ERCOT-Polled Settlement (EPS) Meters at the site (TDSP Project Number 100-BYU). (e) Details of the period of time for which the exemption will apply, including the proposed start and finish dates of that period; and The permanent exemption will start upon the date of approval by the ERCOT Board. There is no end date to this exemption. (f) Any other information requested by ERCOT. ERCOT has not requested any other information to date. Air Liquide’s Bayou-Bayport Complex

##### Key Factors Influencing Issue: On September 25, 2019, TAC unanimously voted to approve Air Liquide’s application for permanent site-specific exemption from compliance with paragraph (6) of Protocol Section 10.3.2.3.

##### Conclusion/Recommendation: As more specifically described above, TAC recommends that the ERCOT Board approve Air Liquide’s application for permanent site-specific exemption from compliance with paragraph (6) of Protocol Section 10.3.2.3.

ELECTRIC RELIABILITY COUNCIL OF TEXAS, INC.

BOARD OF DIRECTORS RESOLUTION

WHEREAS, paragraph (6) of Section 10.3.2.3 of the Electric Reliability Council of Texas, Inc. (ERCOT) Protocols impose requirements related to generation netting for Generation Resource Facilities;

WHEREAS, Air Liquide Large Industries U.S. LP (Air Liquide) has submitted a permanent site-specific exemption application from compliance with paragraph (6) of Protocol Section 10.3.2.3 for the Metering Facilities at the Bayou-Bayport Complex;

WHEREAS, the ERCOT Board of Directors (Board) concurs with the March 31, 2016 Technical Advisory Committee (TAC) recommendation to approve Air Liquide permanent site-specific exemption application; and

WHEREAS, after due consideration of the alternatives, the Board deems it desirable and in the best interest of ERCOT to approve Air Liquide’s permanent site-specific exemption application;

THEREFORE, BE IT RESOLVED, that the ERCOT Board hereby approves Air Liquide’s application for permanent site-specific exemption from compliance with paragraph (6) of Protocol Section 10.3.2.3 for the Bayou-Bayport Complex, including all six ERCOT-Polled Settlement (EPS) Meters at the site as shown on EPS Metering Design Proposal, TDSP Project Number 100-BYU, Meter IDs: BYU_G1, BYU_G2, BYU_G3, BYU_G4, Choate_Plant, BBP_Plant.

CORPORATE SECRETARY’S CERTIFICATE

I, Vickie G. Leady, Assistant Corporate Secretary of ERCOT, do hereby certify that, at its October 8, 2019 meeting, the ERCOT Board passed a motion approving the above Resolution by ______.

IN WITNESS WHEREOF, I have hereunto set my hand this ___ day of October 2019.

______________________________

Vickie G. Leady

Assistant Corporate Secretary

Under Air Liquide and CenterPoint’s historical measurement approach, the interconnection points at the Complex are within 400 yards of each other, but under ERCOT’s approach two of the six interconnection points are 422 yards apart. The other interconnection points are within 400 yards of each other under either approach.