## Slide 1: Planning Geomagnetic Disturbance Task Force (PGDTF) Update to ROS
October 03, 2019
Aster Amahatsion
2019 PGDTF Chair
<number>
Notes: <number>

## Slide 2: PGDTF Meeting
Business meeting was held on September 12th , 2019
Updated the PGDTF scope
Discussed GIC flow for 2022 GIC cases status
  ERCOT has all the modelling data, but has identified PSSE V34.5.1 is not creating transformer GIC flow time series output, which is needed for thermal assessment for transformers. ERCOT is working closely with PTI to resolve the problem.
Discussed frequency of updating GIC models, the approaches recommended include:
    To use metrics of the number of buses and branches differences between cases as a basis.
    Siemens is incorporating PSS®MOD in two years and using that would simplify the case build.
    Vulnerability Assessments have not been done before and may reveal some necessary improvements to the model .
    As ERCOT is located in south and less vulnerable to GMD, no need to build models more frequently.
    The standard requires models to be built at least once in 60 months.
    Based on the discussion we did not have a conclusion on how often we need to update the model. The discussion will continue in future meetings and will need to focus on the vulnerability assessment for now.
<number>
10/03/2019 ROS Meeting
Notes: <number>

## Slide 3
ERCOT presented on the proposed ERCOT implementation timeline for TPL-007-3 Requirements
10/03/2015 ROS Meeting
<number>
PGDTF Meeting

## Slide 4: PGDTF Meeting
Discussed Geomagnetic Disturbance Operations Standard EOP-010-1 and ERCOT GMD operating procedure
The standard requires the posturing (switching or load shedding) the system in response to space weather information should be applied as initial condition before GMD vulnerability assessment study.
PGDTF discussed the current ERCOT GMD operating procedure plan to check for existing system posturing plans. Those plans were drafted from 2015 and were based on limited GMD experiences. Thus operating plans will not be deployed but the voltages in the AC cases will be tuned before the vulnerability study. The results in the vulnerability assessment may cause some changes to the existing operations Procedure.
  Discussed development of the GMD Event outages and the expected format of those outages
  ERCOT expect the outage events to be submitted in a spreadsheet format with confile, and an idev.
  PGDTF is discussing on sharing the outages, since some outages may impact the neighboring TSPs. PGDTF will work on a process to share those events.
Next PGDTF meeting: October 08 at the Met Center (WebEx available)
<number>
10/03/2019 ROS Meeting
Notes: <number>

## Slide 5: Questions
<number>
10/03/2019 ROS Meeting
Notes: <number>