## Slide 1
Energy Storage Resource Energy Deployment Performance (ESREDP)

## Slide 2: Why ESREDP?
Energy storage resources (ESR)* Actual vs Model
  Modeled as a Generation Resource (ESR-GR) and a Controllable Load Resource (ESR-CLR)
  Our system does not recognize that ESR-GR/CLR are part of the same device.
  ESR-GR and ESR-CLR can both receive instructions to perform at the same time, including Base Points, Regulation, and Primary Frequency Response
  The over/under-response of one Resource is not counted towards over/under performance of the other
*Energy storage resource (ESR) is not yet a defined ERCOT term.

## Slide 3: Why ESREDP?
Energy storage resources (ESR)* Actual vs Model (cont.)
  ESR-GR currently scored using Generation Resource Energy Deployment Performance (GREDP)
  ESR-CLR currently scored using Controllable Load Resource Energy Deployment Performance (CLREDP)
  In reality, an ESR is a single device and can only respond in one direction, i.e., ESRs can only consume or inject power at any given instant.
  Goal: Create a metric that captures performance of the ESR as a whole
*Energy storage resource (ESR) is not yet a defined ERCOT term.

## Slide 4: Example
Example 1
QSE holds 50 MW Regulation-Up Responsibility (RURS) on ESR
Telemetered RURS as 25 MW on ESR-GR and 25 MW on ESR-CLR
ESR-CLR Base-Point at 25 MW (charging)
ESR-GR at 0 MW
Both Receive simultaneous Reg-Up Instructions
ESR provides full response by reducing consumption on ESR-CLR

## Slide 5: Example
Chart: ESR-GR REG REQUEST
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
ESR-GR REG REQUEST | 0 | 5 | 10 | 11.5 | 12 | 12.5 | 12 | 11.5 | 10 | 5 | 0
Chart: ESR-CLR REG REQUEST
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
ESR-CLR REG REQUEST | 0 | 5 | 10 | 11.5 | 12 | 12.5 | 12 | 11.5 | 10 | 5 | 0
Chart: ESR REG REQUEST
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
ESR REG REQUEST | 0 | 10 | 20 | 23 | 24 | 25 | 24 | 23 | 20 | 10 | 0

## Slide 6: Example
Chart: ESR-CLR RESPONSE
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
ESR-CLR RESPONSE | 25 | 15 | 5 | 2 | 1 | 0 | 1 | 2 | 5 | 15 | 25
ESR-CLR BP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Chart: ESR-GR RESPONSE
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
ESR-GR RESPONSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ESR-GR BP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chart: ESR RESPONSE
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
ESR RESPONSE | 0 | 10 | 20 | 23 | 24 | 25 | 24 | 23 | 20 | 10 | 0

## Slide 7: Example
Scoring* performance at the individual Resource level using GREDP/CLREDP metrics
Current protocol requirement must have a GREDP/CLREDP less than the greater of 8% or 8 MW  perfect performance gives score of 0% and 0 MW
GREDP (%) | GREDP (MW)
100 | 8.14
CLREDP (%) | CLREDP (MW)
48.25 | 8.14
*Assuming example is across a 5-min period
ATG = Average Telemetered Generation
ARI = Average Regulation Instruction
AEPFR = Average Estimated Primary Frequency Response
ABP = Average Base Point
ATPC = Average Telemetered Power Consumption
ARI = Average Regulation Instruction
AEPFR = Average Estimated Primary Frequency Response
ABP = Average Base Point

## Slide 8: GREDP/CLREDP vs ESREDP (%)
Combining scoring formulas to create an ESR net performance score

## Slide 9: GREDP/CLREDP vs ESREDP (MW)
)

## Slide 10: Example
Scoring* performance using ESREDP
ESREDP (%) | ESREDP (MW)
0 | 0
*Assuming example is across a 5-min period
)
)
)

## Slide 11: Example 2
Example 2
QSE holds 50 MW Regulation-Up Responsibility (RURS) on ESR
Telemetered RURS as 25 MW on ESR-GR and 25 MW on ESR-CLR
ESR-CLR Base-Point at 25 MW (charging)
ESR-GR at 0 MW
Both Receive simultaneous Reg-Up Instructions
ESR provides full response with a combination of reducing consumption on ESR-CLR and injecting with ESR-GR

## Slide 12: Example 2
Chart: GR REG REQUEST
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
GEN REG REQUEST | 0 | 5 | 12.5 | 12.5 | 15 | 15 | 15 | 12.5 | 12.5 | 5 | 0
Chart: CLR REG REQUEST
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
CLR REG REQUEST | 0 | 5 | 12.5 | 12.5 | 15 | 15 | 15 | 12.5 | 12.5 | 5 | 0
Chart: ESR REG REQUEST
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
ESR REG REQUEST | 0 | 10 | 25 | 25 | 30 | 30 | 30 | 25 | 25 | 10 | 0

## Slide 13: Example 2
Chart: GR RESPONSE
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
GEN RESPONSE | 0 | 0 | 0 | 0 | 5 | 5 | 5 | 0 | 0 | 0 | 0
GR BP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chart: CLR RESPONSE
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
CLR RESPONSE | 25 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 25
CLR BP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Chart: ESR RESPONSE
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
ESR RESPONSE | 0 | 10 | 25 | 25 | 30 | 30 | 30 | 25 | 25 | 10 | 0

## Slide 14: Example
Scoring* performance at the individual Resource level using GREDP/CLREDP metrics
Current protocol requirement must have a GREDP/CLREDP less than the greater of 8% or 8 MW  perfect performance gives score of 0% and 0 MW
GREDP (%) | GREDP (MW)
85.71 | 8.18
CLREDP (%) | CLREDP (MW)
52.94 | 8.18
*Assuming example is across a 5-min period

## Slide 15: Example 2
Scoring* performance using ESREDP
ESREDP (%) | ESREDP (MW)
0 | 0
*Assuming example is across a 5-min period
)
)