## Slide 1
ERCOT Frequency Control Report
September 2019
ERCOT
Operations Planning
PDCWG | October 9th, 2019

## Slide 2: Summary of September 2019
CPS1: 175.15%
Current CPS1 12-Month Rolling Average: 174.49%
0 BAAL Exceedance
2 hourly CPS1 score below 100%
BAAL-003 Events have updated through 2018
2018 BAAL-003 FRM Performance: -843.17
2019 RMS1 Statistics
  Mean: 14.90 mHz
  Min: 11.80 mHz
  Max: 18.20 mHz
Energy Statistics
  Total Energy: 37,222,128 MWh
  Wind Energy: 5,975,225 MWh
  Percent Energy from Wind: 16.01%
  Solar Energy: 363,648
  Percent Energy from Solar: 0.97%
Minimum System Inertia
  Mean: 271,107
  Max: 347,090 on Sep 5th
  Min: 224,702 on Sep 29th

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
Sep-19 CPS1 (%): 175.15
Notes: Outliers:
9/13/2019 19:00 96.6%
Large expected generation deviation from conventional units at the beginning of the hour.
9/22/2019 14:00 83.8%
Large expected generation deviation at the top of the hour and two loss of generation events occurred within 5 min at the end of the hour.
9/22/2019 16:00 83.8%
Consistent large expected generation deviation from conventional and solar for 35 minutes during the hour.

## Slide 5: BAAL Exceedances & Violations
There was 0 BAAL exceedances in Sep

## Slide 6: 15-Minute Average CPS1%
Sep-19 CPS1 (%): 175.15

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 174.49%

## Slide 8: Daily RMS1 of ERCOT Frequency by Year
Notes: Mean is 15.19 mHz

## Slide 9: Daily RMS1 of ERCOT Frequency by Month

## Slide 10: Daily RMS1 of ERCOT Frequency by Month
Notes: Mean: 14.90 mHz
Min: 11.80 mHz
Max: 18.20 mHz

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison

## Slide 13: Frequency Profile Comparison

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2018 BAL-003 Selected Events – Update
Notes: BAL-003

## Slide 19: Op. Year 2018 BAL-003 FRM Performance - Update

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 39,226,761 MWh

## Slide 22: Total Energy from Wind Generation
Notes: 6,150,047 MWh

## Slide 23: % Energy from Wind Generation
Notes: 15.68%

## Slide 24: Total Energy From Solar Generation
Notes: 464,456 MWh

## Slide 25: % Energy from Solar Generation
Notes: 1.18%

## Slide 26: ERCOT System Inertia

## Slide 27: Daily Minimum System Inertia
Notes: Minimum Inertia = 128,759 MW*s on 11/3/2018.
Previous Minimum was 130,014 MW*s on 10/27/2017. This was also our record wind day.
Data:
Mean: 271,107
Max: 347,090 on Sep 5th
Min: 224,702 on Sep 29th

## Slide 28: Questions?
Thank you!