## Slide 1
Regulation Bias Analysis Post SCR-773
Sep 2019
ERCOT
Operations Planning
PDCWG | October 9th, 2019

## Slide 2
Discussion Points
Current GTBD Parameters & References
Metric to measure Regulation bias and performance
Regulation Deployed comparison for last three months.
Total Regulation (net) Deployed Comparison
Regulation Deployed 15-minute interval comparison by each hour for 2017, 2018, and 2019 months
Regulation Exhaustion Rate
Regulation bias for consecutive 5-min SCED intervals
Time Error & Contributing Factors
Summary

## Slide 3: Current GTBD Parameters
Notes: 3/12/18 – Integral ACE Time Constant Changed from 60 min to 45 min
5/17/18 - K4 Changed from 0.3 to 0.2 and K5 Changed from 0.4 to 0.5
12/4/18 - K6 Changed from 0 to 0.5
2/12/19 - K6 Changed from 0.5 to 1
4/01/19 - K5 changed from 0.5 to 0.4 and Max. Integral ACE Feedback changed from 250 to 150
4/24/19 - Max. Integral ACE Feedback changed from 150 to 160. PWRR Threshold changed from 20 to 25.
5/22/19 – K5 changed from 0.4 to 0.5 Max. Integral ACE Feedback changed from 160 to 200. PWRR Threshold changed from 25 to 30.

## Slide 4: Projected Wind Ramp Rate MAE
Chart: Hour Ending
Persistence Error | 69.3 | 58.5 | 67.3 | 71.9 | 67.8 | 64.5 | 66.5 | 72.9 | 130.6 | 108.6 | 66.3 | 73.1 | 69.6 | 72.3 | 75.6 | 76.2 | 74.3 | 75.6 | 80.7 | 96.3 | 123.1 | 112.2 | 74.9 | 68
SCED PWRR Error | 54.2 | 48.5 | 51 | 48.3 | 48.1 | 48.6 | 45.1 | 49.3 | 73.3 | 69.5 | 47.8 | 51.6 | 53 | 59 | 64.9 | 65.9 | 68.4 | 65.1 | 66.8 | 65.2 | 76.4 | 61.8 | 54.5 | 61.2

## Slide 5: Projected Wind Ramp Rate Error
Chart: Hour Ending
Persistence Error | 11.9 | 25 | 37.4 | 48.3 | 43.9 | 48.6 | 48.9 | 54.5 | 89 | -61.6 | -15.5 | 19.2 | 13.9 | -4.2 | -24.3 | -25.2 | -26.2 | -30.4 | -12.4 | -2.4 | -106.8 | -101.9 | -49.7 | -3.1
SCED PWRR Error | -11.7 | -11.3 | -4.6 | -1.1 | -3.6 | -1.1 | 4.8 | 7.5 | 20.3 | -51.4 | -4.9 | -0.2 | -8.1 | -15.6 | -17.3 | -17.6 | -19.4 | -24.6 | -11.2 | -22.2 | -58.6 | -47.7 | -25.2 | -11.7
Average Wind HSL | 10971.7 | 10718.9 | 10358.7 | 9840.1 | 9283.3 | 8712.5 | 8150.2 | 7536.2 | 6599 | 6447.7 | 7057.7 | 6947.2 | 6726 | 6649.8 | 6872 | 7163.7 | 7497.3 | 7818.7 | 8138.8 | 8039.4 | 8808.9 | 10157.7 | 11024.9 | 11300.6

## Slide 6: References

## Slide 7
Metrics to Measure SCR-773 Performance
Trend and monitor the regulation deployed by hour.
Set target of 50 MW for total regulation deployed by hour for peak hours.
Set target of 85% for the number of intervals where regulation deployment was both up and down for peak hours.
Track the Regulation exhaustion rate for all hours (not to exceed 5%).
Using a 50MW filter, target 15 occurrences or less per month for regulation bias of six or more consecutive 5 minute intervals for peak hours.

## Slide 8: Total Regulation Deployed Comparison
Total regulation deployed for the last three months.

## Slide 9: Total Regulation Deployed Comparison - Monthly
Chart: Total Regulation Deployed
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Jul-19 | -68.9298 | -88.6599 | -72.4597 | -61.0756 | -29.7471 | -10.1996 | -19.6962 | 36.1109 | -43.2132 | 29.0254 | 95.7585 | 64.4988 | 40.4358 | 22.037 | 45.5324 | 35.5187 | -0.55122 | -25.4521 | -28.1499 | -0.8595 | -1.8404 | -155.882 | -110.9248 | -119.4353
Aug-19 | -103.6202 | -104.5751 | -82.2232 | -62.9126 | -36.4277 | 2.2048 | -18.3044 | 44.3145 | 2.9509 | 18.5765 | 97.3095 | 102.9067 | 63.0842 | 60.9265 | 53.4764 | 59.6469 | 11.0175 | -12.5705 | -12.5094 | 37.2326 | -49.1054 | -157.7212 | -147.4946 | -144.357
Sep-19 | -89.293 | -101.8286 | -82.1636 | -61.3767 | -24.1481 | 15.3461 | 20.2494 | -17.8224 | 15.415 | -13.663 | 25.8291 | 49.3021 | 36.7516 | 49.3529 | 40.4791 | 26.894 | 3.6204 | -36.0844 | -20.4606 | 21.8074 | -131.4417 | -171.6571 | -125.5694 | -123.2886
Threshold (50MW) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50

## Slide 10: Metric 1: Regulation Deployed Comparisons
Trend and monitor the regulation deployed by hour.

## Slide 11: Regulation Deployed Comparison

## Slide 12: Regulation Deployed Comparison
Chart: Regulation-Up Deployed
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Sep-17 | 33.0816 | 24.7567 | 29.1293 | 35.7588 | 45.1572 | 83.1119 | 64.6859 | 43.8171 | 91.196 | 57.8172 | 80.9471 | 108.6186 | 78.6279 | 59.6913 | 43.8682 | 40.2947 | 36.522 | 35.6277 | 43.6863 | 50.0659 | 15.1643 | 27.3782 | 46.6244 | 41.4341
Sep-18 | 44.58 | 28.8156 | 28.0224 | 26.8007 | 42.2949 | 72.5895 | 87.3624 | 43.5235 | 59.5375 | 27.6684 | 40.1573 | 66.0724 | 68.9138 | 44.523 | 48.6969 | 55.3309 | 49.665 | 40.5811 | 56.7139 | 83.439 | 20.1831 | 27.1841 | 39.4379 | 45.8323
Sep-19 | 25.1128 | 9.788 | 9.5914 | 12.4189 | 29.9405 | 64.8705 | 66.4617 | 44.0822 | 65.2028 | 61.9819 | 75.718 | 88.5917 | 84.2245 | 88.342 | 78.6566 | 72.8343 | 54.2041 | 40.1433 | 46.1855 | 74.8553 | 22.0745 | 7.8609 | 21.0917 | 18.2218

## Slide 13: Regulation Deployed Comparison
Chart: Regulation-Down Deployed
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Sep-17 | 77.0627 | 65.1863 | 51.7398 | 40.4217 | 38.4703 | 47.1134 | 48.268 | 57.4091 | 43.0392 | 74.6848 | 49.2417 | 29.9089 | 40.6008 | 46.2569 | 56.0948 | 54.5584 | 64.2921 | 79.1092 | 72.4156 | 70.5684 | 150.5044 | 118.9237 | 97.8038 | 85.4823
Sep-18 | 69.9306 | 67.0137 | 44.3799 | 44.8407 | 42.775 | 54.7925 | 39.0875 | 60.613 | 69.2933 | 117.7622 | 87.4247 | 61.0997 | 46.8526 | 66.7635 | 51.9849 | 48.9871 | 54.1756 | 71.6846 | 55.5865 | 52.7597 | 142.6422 | 127.9728 | 109.8989 | 76.485
Sep-19 | 114.4057 | 111.6166 | 91.755 | 73.7957 | 54.0886 | 49.5244 | 46.2123 | 61.9046 | 49.7877 | 75.6449 | 49.8888 | 39.2895 | 47.4729 | 38.9891 | 38.1774 | 45.9403 | 50.5837 | 76.2276 | 66.6461 | 53.0479 | 153.5162 | 179.518 | 146.6611 | 141.5103

## Slide 14: Metric 2: Total Regulation Deployed Comparisons
Set target of 50MW for total regulation deployed by hour for peak hours.

## Slide 15: Total Regulation Deployed Comparison
Chart: Total Regulation Deployed
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Sep-17 | -43.9811 | -40.4296 | -22.6105 | -4.6629 | 6.6869 | 35.9985 | 16.4179 | -13.5919 | 48.1568 | -16.8676 | 31.7054 | 78.7098 | 38.0271 | 13.4344 | -12.2266 | -14.2638 | -27.7701 | -43.4815 | -28.7293 | -20.5026 | -135.3401 | -91.5455 | -51.1794 | -44.0482
Sep-18 | -25.3506 | -38.1981 | -16.3575 | -18.04 | -0.48007 | 17.797 | 48.2749 | -17.0895 | -9.7557 | -90.0938 | -47.2674 | 4.9727 | 22.0612 | -22.2405 | -3.288 | 6.3437 | -4.5106 | -31.1035 | 1.1273 | 30.6793 | -122.4591 | -100.7886 | -70.4611 | -30.6527
Sep-19 | -89.293 | -101.8286 | -82.1636 | -61.3767 | -24.1481 | 15.3461 | 20.2494 | -17.8224 | 15.415 | -13.663 | 25.8291 | 49.3021 | 36.7516 | 49.3529 | 40.4791 | 26.894 | 3.6204 | -36.0844 | -20.4606 | 21.8074 | -131.4417 | -171.6571 | -125.5694 | -123.2886
Threshold (50MW) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50

## Slide 16: Metric 3: 15-min Intervals Where Both REGUP/REGDN Were Deployed
Set target of 85% for the number of intervals where regulation deployment was both up and down.

## Slide 17: “Zero” Crossing Regulation

## Slide 18: “Zero” Crossing Regulation

## Slide 19: Metric 4: Regulation Exhaustion Rate
Track the regulation exhaustion rate for all hours (not to exceed 5%.)

## Slide 20: Regulation Exhaustion Rate

## Slide 21: Regulation Exhaustion Rate

## Slide 22: Metric 5: Stats on REGUP Bias for Consecutive 5-min Intervals
Using a 50MW filter, target 15 occurrences or less per month for regulation bias of six or more consecutive 5-minute intervals for peak hours.

## Slide 23: Regulation Bias for Consecutive SCED Intervals

## Slide 24: Regulation Bias for Consecutive SCED Intervals
Chart: Regulation-Down Bias
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Sep-17 | 6 | 6 | 5 | 2 | 3 | 2 | 2 | 8 | 3 | 6 | 2 | 1 | 3 | 4 | 3 | 2 | 5 | 6 | 2 | 4 | 22 | 8 | 10 | 5
Sep-18 | 4 | 5 | 2 | 2 | 4 | 3 | 1 | 4 | 7 | 17 | 4 | 3 | 3 | 7 | 5 | 4 | 5 | 6 | 4 | 4 | 18 | 9 | 6 | 5
Sep-19 | 11 | 13 | 14 | 8 | 5 | 1 | 1 | 5 | 3 | 6 | 3 | 3 | 3 | 3 | 1 | 1 | 1 | 3 | 2 | 3 | 15 | 20 | 12 | 10

## Slide 25: Time Error and Contributing Factors
Accumulated Time Error, Load and Wind Ramp, PWRR Error, Start-Up/Shut-Down Hours, STLF Error, and Expected Generation Deviation.

## Slide 26: Time Error Accumulation
Chart: Hourly Accumulated Time Error
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Sep-17 | 5.49 | 3.845 | -0.244 | -1.555 | -0.106 | -2.489 | -1.86 | 2.376 | -3.21 | -3.551 | -4.126 | -6.272 | -4.454 | -3.269 | -0.341 | -1.498 | 1.089 | -0.232 | 2.066 | 0.577 | 4.586 | 5.263 | 4.586 | 4.263
Sep-18 | 5.035 | 1.738 | -1.4 | -2.264 | 0.56 | -0.102 | -3.356 | 4.662 | 0.065 | -0.984 | 2.528 | -0.683 | -3.841 | 2.801 | 1.991 | -3.872 | -1.183 | -2.306 | -4.268 | -7.977 | 5.532 | 2.514 | 6.521 | 0.091
Sep-19 | 3.044 | 5.554 | 8.043 | 6.725 | 4.912 | -0.851 | 0.171 | 0.735 | -1.314 | -0.985 | -6.156 | -3.219 | -1.504 | -3.939 | -5.158 | -9.044 | -8.382 | -2.331 | -3.884 | -5.891 | 4.321 | 7.217 | 5.848 | 6.605

## Slide 27: Load Profile

## Slide 28: Net Load Profile
Chart: ERCOT Total Hourly Load
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Sep-17 | 38155.3261 | 36075.6718 | 34649.1596 | 33769.8711 | 33602.9914 | 34613.8513 | 36783.3951 | 37431.8219 | 38723.2061 | 41330.6603 | 44310.8482 | 47284.7301 | 50018.124 | 52551.0751 | 54420.3105 | 55506.3337 | 56041.6785 | 55544.7074 | 53770.2809 | 51910.5997 | 50742.1864 | 48112.1656 | 44592.9886 | 40962.7678
Sep-18 | 39605.733 | 37746.3989 | 36519.209 | 35814.1631 | 35779.7079 | 36883.6704 | 39011.8088 | 39800.0893 | 40891.389 | 43080.0826 | 45604.3284 | 47968.4239 | 50076.3528 | 51905.957 | 53127.0163 | 53806.1211 | 54102.0735 | 53575.1328 | 52182.9398 | 51008.8139 | 50251.5237 | 48115.7998 | 45071.4466 | 41810.7304
Sep-19 | 44736.292 | 42492.952 | 40915.166 | 39916.9494 | 39664.3237 | 40571.8878 | 42394.1731 | 42946.2918 | 44489.4005 | 47725.878 | 51500.3487 | 55108.9627 | 58355.1595 | 61205.9304 | 63210.4967 | 64353.3917 | 64803.5059 | 64158.7622 | 62244.1997 | 60019.1702 | 58352.2681 | 55385.2554 | 51622.6659 | 47860.2617
Sep-17 | 30046.9777 | 28027.9104 | 26860.0542 | 26386.772 | 26558.9896 | 27876.6964 | 30317.729 | 31233.7285 | 32968.3523 | 35701.5776 | 38419.7463 | 41716.9913 | 44853.3748 | 47475.7701 | 49235.0073 | 50104.4159 | 50391.3731 | 49614.2783 | 47853.9867 | 46115.7009 | 44335.2927 | 40751.1178 | 36783.1752 | 32887.8546
Sep-18 | 32878.4557 | 31227.8786 | 30464.4513 | 30244.4084 | 30539.279 | 31964.7773 | 34277.7049 | 35314.325 | 36649.1489 | 38551.7719 | 40698.6287 | 43131.9135 | 45282.7625 | 47065.8227 | 47960.101 | 48318.7733 | 48297.5761 | 47525.966 | 46096.5638 | 45255.5459 | 44189.3458 | 41352.3755 | 38020.8551 | 34786.4683
Sep-19 | 33986.302 | 31922.8016 | 30676.4527 | 30146.8721 | 30450.0395 | 31902.11 | 34269.9449 | 35405.824 | 37478.945 | 40389.6903 | 43386.9407 | 46986.8432 | 50455.0072 | 53374.8444 | 55262.9142 | 56165.0148 | 56465.3809 | 55635.8986 | 53671.9037 | 51996.8469 | 49730.3812 | 45452.6498 | 40819.2248 | 36731.0507

## Slide 29: Load Ramp

## Slide 30: Wind Profile

## Slide 31: Start-Up & Shut-Down Hours

## Slide 32: Short-Term Load Forecast Error

## Slide 33: STLF Error Chart
Chart: STLF Error
Notes: Min,Max, 10th, 90th percentile
15 minute intervals

## Slide 34: Expected Generation Deviation
Chart: Expected Generation Deviation
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Sep-17 | 9.1897 | 3.3634 | -20.4227 | -54.4464 | -58.386 | -111.0087 | -76.5823 | -29.8695 | -116.8901 | -33.1714 | -103.6267 | -180.9143 | -139.6658 | -125.8965 | -92.6944 | -84.0965 | -58.8616 | -31.0972 | -39.3616 | -27.8298 | 88.3754 | 60.4338 | 10.0474 | 14.5494
Sep-18 | -13.8443 | 2.99 | -29.9839 | -30.4981 | -53.4044 | -63.2834 | -101.342 | -19.8067 | -49.7951 | 46.8973 | -14.6248 | -84.4858 | -95.4456 | -52.1947 | -58.0964 | -64.996 | -59.2667 | -30.6986 | -58.4174 | -110.0169 | 52.7541 | 58.6007 | 28.5949 | 3.0063
Sep-19 | 11.5462 | 20.9399 | 6.6056 | -9.519 | -28.8054 | -76.1773 | -106.0357 | -29.4555 | -88.1466 | 27.8388 | -54.1938 | -138.3139 | -137.9538 | -155.1786 | -136.7138 | -140.1903 | -131.5025 | -71.245 | -85.2794 | -156.8709 | 100.0245 | 168.6139 | 109.1778 | 78.3154

## Slide 35: Expected Generation Deviation

## Slide 36: Expected Generation Deviation

## Slide 37: Questions?
Thank you!