## Slide 1
Southern Cross Transmission Directives
Directive #3 : Ramp rate
October 2019, PDCWG
ERCOT Staff

## Slide 2: Directive #3
ERCOT shall determine what ramp rate restrictions, if any, will be necessary to accommodate the interconnection of the Southern Cross DC tie and shall implement those restrictions and shall certify to the Commission when it has completed these actions.
Upon the interconnection of Southern Cross Transmission DC Tie, there is a potential of up to a 4100 MW change in the DC tie’s schedule (based on the projected maximum import/export capability of the tie).
In order to determine whether ramp rate restrictions should be imposed on the DC tie, ERCOT and PDCWG evaluated;
  the impact to ERCOT’s net load variability due to a DC tie ramp of this magnitude, and
  the impact on ERCOT’s ability to recover from frequency events such as Reportable Balancing Contingency Events during the DC Tie ramps.
  Existing process for managing DC Tie schedules

## Slide 3: Recap of Directive #3 Discussions at PDCWG
ERCOT introduced Southern Cross Directive #3 at the April 2019 PDCWG meeting. Directive_3_Discussion_Points_v3.docx
  At the April 2019 PDCWG meeting, stakeholders requested ERCOT to provide high level overview of how the DC Ties are managed by Control Room today.
  Stakeholders also requested additional data related to usage of regulation during the DC tie ramps as well as historical net load ramp data.
At the June 2019 PDCWG meeting ERCOT presented both the items requested by the stakeholders.
  ERCOT_DC_Tie_Procedure.pptx
The August 2019 PDCWG meeting discussed potential approaches that may be utilized to manage DC Tie Ramps and if any specific restrictions were needed for Southern Cross DC Tie.
    SCT_Directive_3_Rec_PDCWG_Aug2019_v2.pptx
    Follow up with a draft recommendation based on the group’s discussion.

## Slide 4: Proposed Next Step
Under NERC Standard INT-006-4 R1, ERCOT has the authority to reject or curtail an E-Tag that ERCOT does not expect to be capable of supporting either in magnitude or ramp.
Propose to include (high level) specifics on management of DC Tie Schedules due to ramp limitations in the Nodal Protocols.
If system conditions near or in Real-Time show insufficient ramp capability to meet the sum of all DC Ties scheduled ramp, taking into account the full ramping capability of all available Resources and preserving sufficient PRC to avoid EEA triggers, ERCOT may request DC Tie Operators to adjust the ramping of schedule changes and, if still necessary, curtail DC Tie Schedules on last-in-first-out basis and deny any additional e-Tag requests for the impacted intervals.