| NPRR Number | 849 | NPRR Title | Clarification of the Range of Voltage Set Points at a Generation Resource’s POI |
| --- | --- | --- | --- |
| Date of Decision |  | September 12, 2019 |  |
| Action |  | Recommended Approval |  |
| Timeline |  | Normal |  |
| Proposed Effective Date |  | To be determined |  |
| Priority and Rank Assigned |  | To be determined |  |
| Nodal Protocol Sections Requiring Revision |  | 3.15, Voltage Support |  |
| Related Documents Requiring Revision/Related Revision Requests |  | None |  |
| Revision Description |  | This Nodal Protocol Revision Request (NPRR) revises Section 3.15 to clarify the range of voltages at the Point of Interconnection (POI) and circumstances for which a Generation Resource’s reactive capability must be designed to meet. This NPRR does not modify any other provisions within Section 3.15 or its subsections; does not change the Generation Resource’s responsibility to adhere to Voltage Set Points; and does not modify the 2% tolerance band identified in paragraph (4) of Nodal Operating Guide Section 2.7.3.5, Resource Entity Responsibilities and Generation Resource Requirements. Rather, this NPRR simply aims to more clearly specify the reactive capability the Generation Resource must be designed to provide. |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |  |
| Business Case |  | While the Protocols do not expressly prescribe any limit on the range of voltages ERCOT may specify as Voltage Set Points in a Voltage Profile, ERCOT has historically interpreted this range to extend from 0.95 to 1.05 per unit voltage. Based on recent assertions by a developer that the Protocols require a Generation Resource to comply with only one single voltage at the POI (a single season Voltage Profile set point) rather than a range of set points, ERCOT has determined that additional clarification would be helpful. Generation Resources should be capable of supporting system voltage within a range of set points, and an inability to comply with these set points can have a negative impact on reliability by reducing the reactive capability available to the ERCOT System. Generation Resources are the primary source of dynamic reactive capability, and thus serve a critical role in transient and steady-state voltage response to disturbances on the ERCOT System. The clarifications proposed in this NPRR recognize the challenge in providing reactive capability across the entire range of 0.95 to 1.05 per unit voltage. For example, for over-excited (lagging or producing) power factor capability, producing MVARs becomes more difficult at higher voltages. Similarly, for under-excited (leading or absorbing) power factor capability, absorbing MVARs becomes more difficult at lower voltages. In an effort to balance the reactive needs of the system and the challenges Generation Resources face in meeting those needs across a wide range of voltages, ERCOT is proposing to limit the range of voltages that a Generation Resource may be asked to support under normal operating conditions. While lagging capability is generally needed only at lower voltages, and leading capability is generally needed only at higher voltages, there can be times based on system topology and generation/Load patterns where leading capability is needed at voltages less than 1.0 per unit and lagging capability is needed at voltages greater than 1.0 per unit to manage the ERCOT System within steady state voltage limits. The proposed ranges consider these less-common circumstances as well. |  |
| Credit Work Group Review |  | To be determined |  |
| PRS Decision |  | On 10/12/17, PRS unanimously voted to table NPRR849 and refer the issue to ROS. All Market Segments were present for the vote. On 9/12/19, PRS unanimously voted to recommend approval of NPRR849 as amended by the 9/11/19 ERCOT comments. All Market Segments were present for the vote. |  |
| Summary of PRS Discussion |  | On 10/12/17, there was no discussion. On 9/12/19, participants reviewed the 9/11/19 ERCOT comments. |  |

| Sponsor |  |
| --- | --- |
| Name | Stephen Solis |
| E-mail Address | Stephen.solis@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-6772 |
| Cell Number | 512-426-4721 |
| Market Segment | Not applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Cory Phillips |
| E-Mail Address | Cory.phillips@ercot.com |
| Phone Number | 512-248-6464 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| NRG 100517 | Proposed alternative language to describe voltage limits |
| ROS 110317 | Requested PRS continue to table NPRR849 to allow further review by the Operations Working Group (OWG) and the Voltage Profile Working Group (VPWG) |
| ERCOT 120417 | Provided additional clarifications in response to the 10/5/17 NRG comments and feedback provided by OWG and VPWG |
| Invenergy 012518 | Presented a list of concerns with NPRR849, as written, for stakeholder and ERCOT consideration |
| Invenergy 040918 | Reiterated concerns with NPRR849 and requested additional ERCOT studies to substantiate the need for the changes proposed by NPRR849 |
| ERCOT 062118 | Proposed additional edits in response to both sets of Invenergy comments and feedback from the February 23, 2018 NPRR849 workshop |
| E.ON 090718 | Raised a concern with potential inconsistency between compliance language within the Protocols and the North American Electric Reliability Corporation (NERC) Reliability Standards regarding where Voltage Set Points and actual voltages are assessed |
| ERCOT 091818 | Proposed revisions to clarify a Generation Resource’s Real-Time performance obligation to provide reactive capability of at least the amount available under a 0.95 power factor at POI |
| ERCOT 102518 | Proposed additional edits to the 9/18/18 ERCOT comments based on discussions at the September 28, 2018 NPRR849 workshop |
| ERCOT 012219 | Proposed additional edits to the 10/25/18 ERCOT comments to address certain concerns raised at the October 26, 2018 OWG meeting |
| ERCOT 042419 | Proposed additional edits to the 1/22/19 ERCOT comments to address the concerns noted at the February 7, 2019 ROS meeting arising from the usage of the term “as close as practicable” for adherence to Voltage Set Points |
| Joint 042519 | Proposed edits to the original NPRR849 language to address concerns raised by TOs regarding their obligations to supply an identified machine power factor over a specified voltage range at the generator’s POI, and their obligation to change the POI Voltage Set Point, as directed by the respective Transmission and/or Distribution Service Provider (TDSP) or the ERCOT Operator |
| Joint 062119 | Proposed additional edits to the 4/25/19 Joint comments to further incorporate concepts from other filed comments and stakeholder discussions |
| ERCOT 070319 | Proposed additional edits to the 6/21/19 Joint comments |
| ROS 071119 | Endorsed NPRR849 as amended by the 7/3/19 ERCOT comments as revised by ROS |
| ERCOT 071619 | Noted concerns with the language endorsed by ROS and proposed additional edits |
| ERCOT 091119 | Proposed additional clarifications to the 7/16/19 ERCOT comments |

Market Rules Notes

None

Proposed Protocol Language Revision

- 3.15	Voltage Support

(1)	ERCOT, in coordination with the Transmission Service Providers (TSPs), shall establish and update, as necessary, the ERCOT System Voltage Profile and shall post it on the Market Information System (MIS) Secure Area.  ERCOT, the interconnecting TSP, or that TSP’s agent, may modify the Voltage Set Point described in the Voltage Profile based on current system conditions.

(2)	All Generation Resources (including self-serve generating units) that have a gross generating unit rating greater than 20 MVA or those units connected at the same Point of Interconnection (POI) that have gross generating unit ratings aggregating to greater than 20 MVA, that supply power to the ERCOT Transmission Grid, shall provide Voltage Support Service (VSS).

(3)	Except as reasonably necessary to ensure reliability or operational efficiency, TSPs should utilize available static reactive resources prior to requesting a Voltage Set Point change from a Generation Resource.

(4)	Each Generation Resource required to provide VSS shall comply with the following Reactive Power Requirements in Real-Time operations when issued a Voltage Set Point by a TSP or ERCOT:

(a)	An over-excited (lagging or producing) power factor capability of 0.95 or less determined at the generating unit's maximum net power to be supplied to the ERCOT Transmission Grid and for any Voltage Set Point from 0.95 per unit to 1.04 per unit, as measured at the POI;

(b)	An under-excited (leading or absorbing) power factor capability of 0.95 or less, determined at the generating unit's maximum net power to be supplied to the ERCOT Transmission Grid and for any Voltage Set Point from 1.0 per unit to 1.05 per unit, as measured at the POI;

(c)	For any Voltage Set Point outside of the voltage ranges described in paragraphs (a) and (b) above, the Generation Resource shall supply or absorb the maximum amount of Reactive Power available within its inherent capability and the capability of any Var-capable devices as necessary to achieve the Voltage Set Point;

(d) 	When a Generation Resource required to provide VSS is issued a new Voltage Set Point, that Generation Resource shall make adjustments in response to the new Voltage Set Point, regardless of whether the current voltage is within the tolerances identified in paragraph (4) of Operating Guide Section 2.7.3.5, Resource Entity Responsibilities and Generation Resource Requirements;

(e)	Reactive Power capability shall be available at all MW output levels and may be met through a combination of the Generation Resource’s Unit Reactive Limit (URL), which is the generating unit’s dynamic leading and lagging operating capability, and/or dynamic VAr capable devices.  This Reactive Power profile is depicted graphically as a rectangle.  For Intermittent Renewable Resources (IRRs), the Reactive Power requirements shall be available at all MW output levels at or above 10% of the IRR’s nameplate capacity.  When an IRR is operating below 10% of its nameplate capacity and is unable to support voltage at the POI, ERCOT, the interconnecting TSP, or that TSP’s agent may require an IRR to disconnect from the ERCOT System for purposes of maintaining reliability;

(5)	As part of the technical Resource testing requirements prior to the Resource Commissioning Date, all Generation Resources must conduct an engineering study, and demonstrate through performance testing, the ability to comply with the Reactive Power capability requirements in paragraph (4), (7), (8), or (9) of this Section, as applicable.  Any study and testing results must be accepted by ERCOT prior to the Resource Commissioning Date;

(6)	Except for a Generation Resource subject to Planning Guide Section 5.1.1, Applicability, a Generation Resource that has already been commissioned is not required to submit a new reactive study or conduct commissioning-related reactive testing, as described in paragraph (5) above.

(7)	Wind-powered Generation Resources (WGRs) that commenced operation on or after February 17, 2004, and have a signed Standard Generation Interconnection Agreement (SGIA) on or before December 1, 2009 (“Existing Non-Exempt WGRs”), must be capable of producing a defined quantity of Reactive Power to maintain a set point in the Voltage Profile established by ERCOT in accordance with the Reactive Power requirements established in paragraph (4) above, except in the circumstances described in paragraph (a) below.

(a)	Existing Non-Exempt WGRs whose current design does not allow them to meet the Reactive Power requirements established in paragraph (4) above must conduct an engineering study using the Summer/Fall 2010 on-peak/off-peak Voltage Profiles, or conduct performance testing to determine their actual Reactive Power capability.  Any study or testing results must be accepted by ERCOT.  The Reactive Power requirements applicable to these Existing Non-Exempt WGRs will be the greater of: the leading and lagging Reactive Power capabilities established by the Existing Non-Exempt WGR’s engineering study or testing results; or Reactive Power proportional to the real power output of the Existing Non-Exempt WGR (this Reactive Power profile is depicted graphically as a triangle) sufficient to provide an over-excited (lagging) power factor capability of 0.95 or less and an under-excited (leading) power factor capability of 0.95 or less, both determined at the WGR’s set point in the Voltage Profile established by ERCOT, and both measured at the POI.

(i)	Existing Non-Exempt WGRs shall submit the engineering study results or testing results to ERCOT no later than five Business Days after its completion.

(ii)	Existing Non-Exempt WGRs shall update any and all Resource Registration data regarding their Reactive Power capability documented by the engineering study results or testing results.

(iii)	If the Existing Non-Exempt WGR’s engineering study results or testing results indicate that the WGR is not able to provide Reactive Power capability that meets the triangle profile described in paragraph (7)(a) above, then the Existing Non-Exempt WGR will take steps necessary to meet that Reactive Power requirement depicted graphically as a triangle by a date mutually agreed upon by the Existing Non-Exempt WGR and ERCOT.  The Existing Non-Exempt WGR may meet the Reactive Power requirement through a combination of the WGR’s URL and/or automatically switchable static VAr capable devices and/or dynamic VAr capable devices.  No later than five Business Days after completion of the steps to meet that Reactive Power requirement, the Existing Non-Exempt WGR will update any and all Resource Registration data regarding its Reactive Power and provide written notice to ERCOT that it has completed the steps necessary to meet its Reactive Power requirement.

(iv)	For purposes of measuring future compliance with Reactive Power requirements for Existing Non-Exempt WGRs, results from performance testing or the Summer/Fall 2010 on-peak/off-peak Voltage Profiles utilized in the Existing Non-Exempt WGR’s engineering study shall be the basis for measuring compliance, even if the Voltage Profiles provided to the Existing Non-Exempt WGR are revised for other purposes.

(b)	Existing Non-Exempt WGRs whose current design allows them to meet the Reactive Power requirements established in paragraph (4) above (depicted graphically as a rectangle) shall continue to comply with that requirement.  ERCOT, with cause, may request that these Existing Non-Exempt WGRs provide further evidence, including an engineering study, or performance testing, to confirm accuracy of Resource Registration data supporting their Reactive Power capability.

(8)	Qualified Renewable Generation Resources (as described in Section 14, State of Texas Renewable Energy Credit Trading Program) in operation before February 17, 2004, required to provide VSS and all other Generation Resources required to provide VSS that were in operation prior to September 1, 1999, whose current design does not allow them to meet the Reactive Power requirements established in paragraph (4) above, will be required to maintain a Reactive Power requirement as defined by the Generation Resource’s URL that was submitted to ERCOT and established per the criteria in the ERCOT Operating Guides.

(9)	New generating units connected before May 17, 2005, whose owners demonstrate to ERCOT’s satisfaction that design and/or equipment procurement decisions were made prior to February 17, 2004, based upon previous standards, whose design does not allow them to meet the Reactive Power requirements established in paragraph (4) above, will be required to maintain a Reactive Power requirement as defined by the Generation Resource’s URL that was submitted to ERCOT and established per the criteria in the Operating Guides.

(10)	For purposes of meeting the Reactive Power requirements in paragraphs (4) through (9) above, multiple generation units including IRRs shall, at a Generation Entity’s option, be treated as a single Generation Resource if the units are connected to the same transmission bus.

(11)	Generation Entities may submit to ERCOT specific proposals to meet the Reactive Power requirements established in paragraph (4) above by employing a combination of the URL and added VAr capability, provided that the added VAr capability shall be automatically switchable static and/or dynamic VAr devices.  A Generation Resource and TSP may enter into an agreement in which the proposed static VAr devices can be switchable using Supervisory Control and Data Acquisition (SCADA).  ERCOT may, at its sole discretion, either approve or deny a specific proposal, provided that in either case, ERCOT shall provide the submitter an explanation of its decision.

(12)	A Generation Resource and TSP may enter into an agreement in which the Generation Resource compensates the TSP to provide VSS to meet the Reactive Power requirements of paragraph (4) above in part or in whole.  The TSP shall certify to ERCOT that the agreement complies with the Reactive Power requirements of paragraph (4).

(13)	Unless specifically approved by ERCOT, no unit equipment replacement or modification at a Generation Resource shall reduce the capability of the unit below the Reactive Power requirements that applied prior to the replacement or modification.

(14)	Generation Resources shall not reduce high reactive loading on individual units during abnormal conditions without the consent of ERCOT unless equipment damage is imminent.

(15)	All WGRs must provide a Real-Time SCADA point that communicates to ERCOT the number of wind turbines that are available for real power and/or Reactive Power injection into the ERCOT Transmission Grid.  WGRs must also provide two other Real-Time SCADA points that communicate to ERCOT the following:

(a)	The number of wind turbines that are not able to communicate and whose status is unknown; and

(b)	The number of wind turbines out of service and not available for operation.

(16)	All PhotoVoltaic Generation Resources (PVGRs) must provide a Real-Time SCADA point that communicates to ERCOT the capacity of PhotoVoltaic (PV) equipment that is available for real power and/or Reactive Power injection into the ERCOT Transmission Grid.  PVGRs must also provide two other Real-Time SCADA points that communicate to ERCOT the following:

(a)	The capacity of PV equipment that is not able to communicate and whose status is unknown; and

(b)	The capacity of PV equipment that is out of service and not available for operation.

(17)	For the purpose of complying with the Reactive Power requirements under this Section 3.15, Reactive Power losses that occur on privately-owned transmission lines behind the POI may be compensated by automatically switchable static VAr capable devices.