| NOGRR Number | 191 | NOGRR Title | Related to NPRR939, Modification to Load Resources Providing RRS to Maintain Minimum PRC on Generators During Scarcity Conditions |
| --- | --- | --- | --- |
| Date of Decision |  | October 8, 2019 |  |
| Action |  | Approved |  |
| Timeline |  | Normal |  |
| Effective Date |  | Upon system implementation of Nodal Protocol Revision Request (NPRR) 939, Modification to Load Resources Providing RRS to Maintain Minimum PRC on Generators During Scarcity Conditions |  |
| Priority and Rank Assigned |  | Not applicable |  |
| Nodal Operating Guide Sections Requiring Revision |  | 4.8.1, Responsive Reserve Service Manual Deployment |  |
| Related Documents Requiring Revision/Related Revision Requests |  | NPRR939 |  |
| Revision Description |  | This Nodal Operating Guide Revision Request (NOGRR), along with NPRR939, allows ERCOT to manually deploy Load Resources other than Controllable Load Resources providing Responsive Reserve (RRS) to maintain a minimum 500 MWs of Physical Responsive Capability (PRC) reserves on Generation Resources to continuously balance the Demand with supply while maintaining the stable grid frequency for smaller disturbances. |  |
| Reason for Revision |  | Addresses current operational issues. Meets Strategic goals (tied to the ERCOT Strategic Plan or directed by the ERCOT Board). Market efficiencies or enhancements Administrative Regulatory requirements Other: (explain) (please select all that apply) |  |
| Business Case |  | The current language dividing Load Resources providing RRS into just two groups may result in much larger manual deployments than needed. Under certain tight conditions, if Load Resources providing RRS were contributing up to 150% of their RRS Ancillary Service Resource Responsibilities towards PRC, then during those conditions there is a potential for ERCOT to have PRC as high as 2,700 MWs all on Load Resources. |  |
| ROS Decision |  | On 7/11/19, ROS unanimously voted to recommend approval of NOGRR191 as submitted. All Market Segments were present for the vote. On 8/8/19, ROS unanimously voted to endorse and forward to TAC the 7/11/19 ROS Report and the Impact Analysis for NOGRR191. All Market Segments were present for the vote. |  |
| Summary of ROS Discussion |  | On 7/11/19, there was no discussion. On 8/8/19, there was no discussion. |  |
| TAC Decision |  | On 9/25/19, TAC unanimously voted to recommend approval of NOGRR191 as recommended by ROS in the 8/8/19 ROS Report. All Market Segments were present for the vote. |  |
| Summary of TAC Discussion |  | On 9/25/19, there was no discussion. |  |
| ERCOT Opinion |  | ERCOT supports approval of NOGRR191. |  |
| Board Decision |  | On 10/8/19, the ERCOT Board approved NOGRR191 as recommended by TAC in the 9/25/19 TAC Report as amended by the 9/26/19 ERCOT comments. |  |

| Sponsor |  |
| --- | --- |
| Name | Sandip Sharma |
| E-mail Address | sandip.sharma@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-4298 |
| Cell Number |  |
| Market Segment | Not applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Phillip Bracy |
| E-Mail Address | Phillip.Bracy@ercot.com |
| Phone Number | 512-248-6917 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| ERCOT 092619 | Aligned proposed language in NOGRR191 with the incorporation of NOGRR187, Related to NPRR863, Creation of ERCOT Contingency Reserve Service and Revisions to Responsive Reserve, into the Nodal Operating Guide. |

Market Rules Notes

Please note the baseline language in the following sections has been updated to reflect incorporation of the following NOGRR into the Nodal Operating Guide:

- NOGRR187, Related to NPRR863, Creation of ERCOT Contingency Reserve Service and Revisions to Responsive Reserve (Incorporated 9/1/19)

  - Section 4.8.1

Please note that the following NOGRR(s) also propose revisions to the following section(s):

- NOGRR197, Align Responsive Reserve (RRS) Manual Deployment Requirements with Current Practice

  - Section 4.8.1

Proposed Guide Language Revision

- 4.8.1	Responsive Reserve Service Manual Deployment

(1)	RRS for capacity may be manually deployed (HASL released) when the system approaches scarcity conditions so that the capacity reserved behind HASL will be released to Security-Constrained Economic Dispatch (SCED).

(a)	When HASL – (Gen + 5 minute load ramp) <= 200 MW, ERCOT may deploy the available RRS capacity from Generation Resources and Controllable Load Resources in 500 MW increments after all the available Non-Spinning Reserve (Non-Spin) service has been deployed and Resources have responded to any earlier deployments.

(b)	When HSL – (Gen + 5 minute load ramp) <= 500 MW, ERCOT may deploy Load Resources controlled by high-set under-frequency relays providing RRS.

[NOGRR187: Replace paragraph (1) above with the following upon system implementation of NPRR863:] (1) RRS for capacity may be manually deployed (HASL released) when the system approaches scarcity conditions so that the capacity reserved behind HASL will be released to SCED. (a) When HASL – (Gen + 5 minute load ramp) <= 200 MW, ERCOT may deploy the available RRS capacity from Generation Resources and Controllable Load Resources in 500 MW increments after all the available ECRS (dispatchable by SCED) and Non-Spinning Reserve (Non-Spin) service has been deployed and Resources have not responded to any earlier deployments. (b) When HSL – (Gen + 5 minute load ramp) <= 500 MW, ERCOT may deploy Load Resources controlled by high-set under-frequency relays providing RRS.