## Slide 1: Line on Outage as Binding Constraint
6101_A on September 27 and 28, 2019
Patrick de Man
Geodesic Energy LLC

## Slide 2: Timeline of Events
Scheduled outage of line 6101_A (NOTSW to CHEYT)
Congestion
ERCOT notified early Saturday morning
  Emails to Client Services and Shift Supervisors
Congestion continued
Line 6101_A reinstated on 9/28 at 18:43
OutageIdentifier | PlannedStartDate | PlannedEndDate | ActualStartDate | ActualEndDate | SubmitTime
ONC00383052 | 9/27/2019 18:01 | 7/31/2020 18:00 | 9/27/2019 18:01 |  | 8/20/2019 15:10
 |  |  | HE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
Date | Constraint | Contingency | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
9/27/2019 | 6101__A | SECNMO28 | 58 | 29 | 15 | 28 | 0 | 0 |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0 | 17 | 23 | 38
9/28/2019 | 6101__A | SECNMO28 | 0 | 4 | 47 | 26 | 0 | 0 | 0 | 0 | 0 |  |  |  |  |  |  |  |  |  |  | 35 | 164 | 115 | 91 | 60
 |  |  | HE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
Date | Constraint | Contingency | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
9/28/2019 | 6101__A | DWINDUN8 |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0 | 29 | 26 | 25 | 60 | 140 | 0 | 0 | 0 | 0
9/28/2019 | 6101__A | DYKNWIN8 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 4 |  |  |  |  |  | 

## Slide 3
What exactly allowed this situation to occur?
How can such inconsistency persist for 24+ hours?
  Inconsistently should throw up an alert at first occurrence
  ERCOT notified, but no action until many hours later
How frequently does this occur?
What was known during bidding into DAM?
Error caused by ERCOT or ONCOR? Repricing?
Issues