## Slide 1
Dan Woodfin
Senior Director, System Operations
Calvin Opheim
Manager, Load Forecasting
ERCOT
WMWG
October 21, 2019
Analysis of Load Forecast Selection

## Slide 2: Outline
Overall forecast model accuracy
Overall model selection
Large forecast error analysis
Model selection for large forecast errors
Summer peak hour forecast analysis
- Unless noted otherwise, data based on all hours January – September 2019
- See the appendix for a description of the 7 models

## Slide 3: One-day-ahead load forecast error (actual load - load forecast)
Positive: Under-forecast Errors
Negative:Over-forecast Errors

## Slide 4: Three-day-ahead load forecast error (actual load - load forecast)

## Slide 5: Seven-day-ahead load forecast error (actual load - load forecast)

## Slide 6: Selected Model Frequency
Chart: Percent of Hours
| 1-d-ahead Selection Ratio | 3-d-ahead Selection Ratio | 7-d-ahead Selection Ratio
A3 | 0.040293 | 0.16117 | 0.20513
A6 | 0.043956 | 0.18315 | 0.13919
E | 0.28205 | 0.2381 | 0.15751
E1 | 0.11355 | 0.084249 | 0.12821
E2 | 0.076923 | 0.047619 | 0.03663
E3 | 0.30769 | 0.21612 | 0.25641
M | 0.13553 | 0.069597 | 0.076923
Total Hours: 273 days·24 hours/day=6,552 hours (Jan. 2019-Sep. 2019)

## Slide 7: 1-day-ahead model performance
*Best load forecast model has smallest absolute forecast error
Chart: 1-d-ahead model performance
| 1st | 2nd | 3rd | 4th | 5th | 6th | 7th
A3 | 0.1441 | 0.15051 | 0.091742 | 0.081667 | 0.11113 | 0.2392 | 0.18165
A6 | 0.14837 | 0.13387 | 0.086552 | 0.067165 | 0.10655 | 0.1989 | 0.25859
E | 0.14822 | 0.15799 | 0.15677 | 0.12975 | 0.15051 | 0.14089 | 0.11586
E1 | 0.15341 | 0.14517 | 0.14639 | 0.12105 | 0.15906 | 0.13555 | 0.13937
E2 | 0.15021 | 0.13158 | 0.10624 | 0.10533 | 0.13555 | 0.14074 | 0.23035
E3 | 0.14914 | 0.17982 | 0.17524 | 0.14883 | 0.14257 | 0.13036 | 0.074034
M | 0.10655 | 0.10105 | 0.23722 | 0.34621 | 0.19447 | 0.014349 | 0.00015265
Selected Model | 0.14181 | 0.15127 | 0.16227 | 0.15998 | 0.14593 | 0.12777 | 0.11098
best load forecast model
Notes: X axis shows the frequency of whether a particular forecast model has been the most accurate (1st) or the least accurate (7th)

## Slide 8: 3-day-ahead model performance
Chart: 3-d-ahead model performance
| 1st | 2nd | 3rd | 4th | 5th | 6th | 7th
A3 | 0.1554 | 0.16059 | 0.087773 | 0.075256 | 0.10212 | 0.23996 | 0.1789
A6 | 0.1644 | 0.13525 | 0.086246 | 0.061823 | 0.10029 | 0.19829 | 0.2537
E | 0.14334 | 0.167 | 0.1673 | 0.12868 | 0.13998 | 0.13937 | 0.11433
E1 | 0.15524 | 0.16364 | 0.15387 | 0.11891 | 0.14639 | 0.14044 | 0.12151
E2 | 0.15601 | 0.1154 | 0.11555 | 0.092047 | 0.14502 | 0.13464 | 0.24134
E3 | 0.14639 | 0.17768 | 0.16883 | 0.13509 | 0.15082 | 0.13097 | 0.090215
M | 0.079225 | 0.080751 | 0.22012 | 0.38819 | 0.21554 | 0.016181 | 0
Selected Model | 0.15677 | 0.14761 | 0.13189 | 0.12273 | 0.14547 | 0.13479 | 0.16074
best load forecast model

## Slide 9: 7-day-ahead model performance
Chart: 7-d-ahead model performance
| 1st | 2nd | 3rd | 4th | 5th | 6th | 7th
A3 | 0.16181 | 0.18089 | 0.083804 | 0.060296 | 0.094337 | 0.21951 | 0.19936
A6 | 0.16883 | 0.16425 | 0.086094 | 0.059075 | 0.090368 | 0.20669 | 0.2247
E | 0.15646 | 0.17051 | 0.15769 | 0.11922 | 0.13067 | 0.16242 | 0.10304
E1 | 0.12471 | 0.15036 | 0.17448 | 0.11617 | 0.15906 | 0.14013 | 0.13509
E2 | 0.19173 | 0.12334 | 0.10517 | 0.10609 | 0.12349 | 0.1267 | 0.22348
E3 | 0.14181 | 0.1612 | 0.16608 | 0.1325 | 0.15723 | 0.12685 | 0.11433
M | 0.054648 | 0.049458 | 0.22668 | 0.40681 | 0.2447 | 0.017707 | 0
Selected Model | 0.15143 | 0.13326 | 0.12013 | 0.11525 | 0.1383 | 0.15814 | 0.18348
best load forecast model

## Slide 10: one-day-ahead large load forecast errors (actual load - load forecast)
Chart: one-day-ahead large load forecast errors (actual load - load forecast)
Selected Model | 6135.4585 | 6145.5451 | 6172.9934 | 6178.4341 | 6208.5386 | 6213.7291 | 6348.1855 | 6386.4541 | 6449.3105 | 6451.4563 | 6458.36 | 6495.0726 | 6524.8647 | 6640.2935 | 6649.7479 | 6661.1212 | 6676.302 | 6699.8518 | 6811.9842 | 6895.3573 | 6911.2579 | 6912.5539 | 6963.0014 | 6988.8955 | 7027.0523 | 7090.6171 | 7094.5988 | 7142.0626 | 7167.971 | 7212.8303 | 7261.6786 | 7409.2773 | 7652.5742 | 8037.0152 | 8146.2898 | 8189.9846 | 8211.377 | 9254.0065 | 9386.6663 | 9402.0425 | 9505.7874
A3 | 6095.4155 | 7094.4162 | 7275.6965 | 8389.8638 | 6320.4566 | 8538.0377 | 8610.6113 | 8829.0088 | 8467.9902 | 6451.4563 | 7259.692 | 7496.6976 | 6524.8647 | 6656.8443 | 8141.951 | 7778.2462 | 7199.1614 | 9004.7346 | 7711.0311 | 8286.7323 | 7718.711 | 6912.5539 | 6795.7787 | 6562.9619 | 7138.7398 | 7317.2265 | 7094.5988 | 7778.6641 | 7265.7523 | 8385.346 | 8140.913 | 7833.9257 | 9420.6328 | 10171.2183 | 9249.1257 | 9662.6721 | 9817.4746 | 10698.9596 | 10601.3304 | 10880.6206 | 11182.4671
A6 | 6057.5718 | 7442.4123 | 7354.1575 | 8484.6685 | 7143.5698 | 8734.8346 | 9766.5058 | 9287.3448 | 8559.2715 | 6294.261 | 8982.6764 | 8928.7171 | 6386.603 | 5634.7896 | 9350.3534 | 7871.1915 | 7663.2708 | 9359.0471 | 9976.0428 | 9862.8964 | 8149.8126 | 6805.5226 | 6385.5405 | 6364.2275 | 6279.0719 | 6573.3398 | 7057.4034 | 9017.0782 | 8369.2992 | 8401.3303 | 10279.5848 | 9659.8007 | 10553.3242 | 11388.7262 | 9669.9851 | 11174.8752 | 10985.7637 | 12140.6393 | 11383.9007 | 12260.3003 | 12409.3109
E | 6423.9585 | 5714.5373 | 5433.9114 | 6059.356 | 6208.5386 | 5929.2409 | 6831.9824 | 6029.9151 | 6282.8965 | 6789.136 | 6458.36 | 5785.4358 | 6380.9937 | 6788.7935 | 7023.0487 | 6496.4415 | 6652.759 | 6396.1721 | 6811.9842 | 6051.9979 | 6718.6095 | 7037.6242 | 7090.3022 | 6974.9971 | 7106.7515 | 7285.414 | 7455.6652 | 7142.0626 | 7167.971 | 6585.1975 | 7261.6786 | 7409.2773 | 7821.9727 | 8477.2144 | 7890.2976 | 7342.4143 | 8350.0801 | 8941.2174 | 8961.7288 | 9200.105 | 9175.7327
E1 | 6136.3569 | 6927.8342 | 6054.3098 | 5693.2544 | 5607.937 | 6124.5416 | 5886.2832 | 5920.0166 | 6027.3965 | 6448.0344 | 4691.6608 | 6859.2366 | 6191.896 | 7130.2935 | 6121.9471 | 6645.9415 | 7105.0559 | 6041.3674 | 5619.4842 | 7599.4979 | 7347.211 | 6955.2218 | 6828.3998 | 6803.794 | 7689.2515 | 7325.1171 | 6996.6652 | 6299.6641 | 6164.6702 | 7089.596 | 6002.5809 | 5921.1757 | 6572.375 | 7582.9176 | 7872.5945 | 8937.0158 | 7198.2793 | 9836.2174 | 10130.3304 | 10051.105 | 9729.9359
E2 | 5886.3569 | 5596.5373 | 6040.1106 | 5079.9537 | 5904.0386 | 4967.4401 | 5620.6855 | 5465.0166 | 5447.2988 | 5795.636 | 5696.0631 | 5825.3382 | 5673.1929 | 4864.5943 | 5562.9471 | 6219.043 | 6277.3567 | 5663.2737 | 6164.0858 | 6258.2948 | 6476.711 | 6276.7218 | 5785.7006 | 6084.4971 | 5285.5523 | 5662.914 | 6502.0636 | 7057.2657 | 6896.471 | 6702.5022 | 6834.6786 | 7197.1757 | 6334.875 | 6809.2145 | 7604.196 | 7194.2111 | 6712.4785 | 7996.1237 | 8540.8304 | 8392.605 | 8801.6312
E3 | 6135.4585 | 5394.3342 | 6060.9114 | 5669.6529 | 6405.8394 | 5509.1393 | 6348.1855 | 5688.0166 | 6021.0996 | 6279.9368 | 5854.6608 | 6508.7366 | 6144.2944 | 6640.2935 | 6649.7479 | 6166.1446 | 6147.1575 | 6393.6721 | 6618.8866 | 6280.0956 | 6295.1095 | 6569.1242 | 6963.0014 | 6988.8955 | 7027.0523 | 7090.6171 | 7046.5636 | 6473.3594 | 6612.2679 | 7301.4006 | 6892.2802 | 6573.6757 | 7652.5742 | 8037.0152 | 8115.2976 | 7813.6096 | 8211.377 | 8797.4205 | 8698.932 | 8485.8081 | 8639.2327
M | 6122.5249 | 6145.5451 | 6172.9934 | 6178.4341 | 6265.0738 | 6213.7291 | 7177.3535 | 6386.4541 | 6449.3105 | 6343.054 | 6490.4928 | 6495.0726 | 6216.9624 | 6285.9498 | 7141.6698 | 6661.1212 | 6676.302 | 6699.8518 | 7150.2303 | 6895.3573 | 6911.2579 | 6759.4367 | 6641.4858 | 6629.8955 | 6754.4078 | 6875.8124 | 7025.4933 | 7294.6641 | 7079.4163 | 7212.8303 | 7568.6161 | 7432.496 | 8059.2813 | 8744.3746 | 8146.2898 | 8189.9846 | 8545.9317 | 9254.0065 | 9386.6663 | 9402.0425 | 9505.7874
41 hours out of 6,552 hours when 1-d-ahead load forecast error > 6000 MW

## Slide 11: one-day-ahead large load forecast errors (actual load - load forecast)
34 hours out of 6,552 hours when 1-d-ahead load forecast error < -4000 MW
Chart: one-day-ahead large load forecast errors (actual load - load forecast)
Selected Model | -5718.4959 | -5420.8938 | -5403.2814 | -5234.543 | -4973.4672 | -4934.4414 | -4785.0727 | -4729.3752 | -4727.4615 | -4723.8344 | -4705.8376 | -4629.2769 | -4580.0985 | -4569.1831 | -4518.9887 | -4504.7353 | -4495.6766 | -4488.1808 | -4486.4854 | -4480.1927 | -4471.861 | -4406.972 | -4406.2086 | -4383.9479 | -4370.0927 | -4311.5222 | -4257.8077 | -4252.7144 | -4208.4705 | -4164.7104 | -4148.9454 | -4144.9633 | -4119.5214 | -4053.7836
A3 | -4128.4763 | -4413.9798 | -4175.9181 | -4250.6484 | -4236.0727 | -4438.4062 | -4285.0493 | -4924.6057 | -3961.735 | -4397.5531 | -4105.0524 | -4235.8472 | -4026.411 | -3967.562 | -4414.7621 | -3894.8135 | -4304.1766 | -4049.0324 | -4176.9386 | -4199.5091 | -4368.2712 | -4264.7767 | -4150.0485 | -4124.7487 | -4633.5615 | -4727.0027 | -3835.2725 | -3725.9722 | -3506.0565 | -4501.0932 | -4427.7735 | -4660.1742 | -4915.6933 | -3297.2211
A6 | -4695.5232 | -4414.8157 | -4500.129 | -4474.6836 | -4924.186 | -4577.5625 | -4414.4946 | -4884.7776 | -4407.6568 | -4723.8344 | -4689.2985 | -4629.2769 | -4021.4149 | -3979.7261 | -4407.1293 | -3892.5205 | -4495.6766 | -4100.5324 | -4376.0362 | -4466.3645 | -4628.5524 | -4339.3939 | -4406.2086 | -4208.1002 | -3733.6123 | -4775.323 | -4257.8077 | -4285.2808 | -3834.4393 | -4471.8588 | -4397.2657 | -3958.9945 | -4042.6308 | -3807.0961
E | -2155.8943 | -3728.097 | -2366.5822 | -2411.8437 | -2410.2641 | -2790.1406 | -5349.518 | -4278.0745 | -2130.86 | -9265.1469 | -2044.9391 | -9192.5425 | -4129.6415 | -4231.5932 | -4716.6918 | -4712.708 | -8821.7547 | -4367.6808 | -4874.4854 | -4923.1927 | -4996.6618 | -4917.3705 | -8977.5133 | -4641.5495 | -3815.0927 | -4518.823 | -8410.6397 | -1868.4137 | -4000.0799 | -4385.0112 | -4523.3438 | -3607.7641 | -4766.4238 | -2081.6821
E1 | -5438.4959 | -5860.097 | -5032.5822 | -4300.7422 | -5430.2641 | -5113.9414 | -4713.3149 | -4175.6721 | -5060.7623 | -7389.0492 | -5758.9391 | -6984.3433 | -5239.2391 | -4851.9956 | -4314.891 | -4919.5088 | -7033.5516 | -4488.1808 | -4486.4854 | -4480.1927 | -4471.861 | -4406.972 | -6788.5133 | -4383.9479 | -4519.5927 | -4286.4245 | -5609.4405 | -4742.816 | -4270.6776 | -3740.8081 | -4071.5431 | -5272.8617 | -4841.7245 | -4989.1821
E2 | -2302.9958 | -3985.2962 | -2918.379 | -3121.543 | -2353.7641 | -3420.9414 | -5563.9165 | -4353.5745 | -2350.7623 | -6875.3461 | -2290.1384 | -6916.6402 | -5012.1415 | -5289.2925 | -4518.9887 | -5356.6103 | -6820.3524 | -4511.7824 | -4735.9854 | -4593.7942 | -4783.861 | -4744.2689 | -6501.1149 | -4628.0495 | -4221.1943 | -4354.6237 | -6303.7413 | -1959.316 | -4635.0799 | -4204.5112 | -4148.9454 | -4217.3617 | -3759.2245 | -1526.7836
E3 | -5718.4959 | -5420.8938 | -5403.2814 | -5234.543 | -4973.4672 | -4934.4414 | -4384.1157 | -4729.3752 | -4727.4615 | -7979.0492 | -4705.8376 | -7922.7417 | -5051.9384 | -5094.9956 | -4152.2895 | -4252.208 | -6998.7547 | -4426.0832 | -4624.8878 | -4441.595 | -4293.7594 | -4680.1713 | -8166.7164 | -4631.7487 | -4370.0927 | -4311.5222 | -6844.1397 | -4252.7144 | -5004.4783 | -4164.7104 | -4259.2462 | -4144.9633 | -4119.5214 | -4053.7836
M | -4073.3357 | -4637.2141 | -4066.129 | -3965.6484 | -4054.6703 | -4212.5664 | -4785.0727 | -4557.676 | -3773.2193 | -6771.6508 | -3932.3493 | -6646.9058 | -4580.0985 | -4569.1831 | -4420.7855 | -4504.7353 | -6412.3563 | -4323.8762 | -4545.7979 | -4517.4466 | -4590.486 | -4558.8275 | -6498.3453 | -4436.3502 | -4215.5263 | -4495.6042 | -5876.8233 | -3472.4058 | -4208.4705 | -4244.6557 | -4304.6759 | -4310.3695 | -4407.5292 | -3292.643

## Slide 12: three-day-ahead large load forecast errors (actual load - load forecast)
Chart: three-day-ahead large load forecast errors (actual load - load forecast)
69 hours out of 6,552 hours when 3-d-ahead load forecast error > 6000 MW

## Slide 13: three-day-ahead large load forecast errors (actual load - load forecast)
59 hours out of 6,552 hours when 3-d-ahead load forecast error < -4000 MW
Chart: three-day-ahead large load forecast errors (actual load - load forecast)
Selected Model | -8474.3966 | -8349.0163 | -8102.666 | -8084.5782 | -7795.2845 | -7774.1378 | -7714.6187 | -7667.8495 | -7567.151 | -7345.1184 | -7256.9348 | -7241.7364 | -7099.4437 | -7097.4313 | -6912.6055 | -6908.1032 | -6766.6533 | -6756.7224 | -6677.1379 | -6605.8775 | -6593.7864 | -6520.0644 | -6476.1167 | -6432.7943 | -6255.5069 | -6236.3496 | -6208.7722 | -6196.3273 | -6154.6366 | -6125.7593 | -6035.8072 | -6028.461 | -5963.1935 | -5870.4159 | -5839.7875 | -5818.2656 | -5788.7212 | -5772.1693 | -5763.5882 | -5680.0541 | -5573.6761 | -5565.6058 | -5504.6798 | -5449.6237 | -5438.0059 | -5433.2641 | -5428.4825 | -5350.7422 | -5322.9391 | -5319.3509 | -5307.1791 | -5295.8402 | -5277.1875 | -5243.9091 | -5240.8679 | -5203.5982 | -5142.1256 | -5137.5004 | -5035.7836
A3 | -8474.3966 | -8349.0163 | -8102.666 | -8084.5782 | -7795.2845 | -7774.1378 | -7714.6187 | -7667.8495 | -7567.151 | -7345.1184 | -7256.9348 | -7241.7364 | -7099.4437 | -7097.4313 | -6912.6055 | -4751.1813 | -5290.1025 | -6756.7224 | -6677.1379 | -4124.4283 | -4730.2747 | -6520.0644 | -4962.1246 | -5518.6068 | -6137.7999 | -6236.3496 | -6327.2761 | -6196.3273 | -4911.1639 | -3491.4351 | -5699.4986 | -6028.461 | -5079.2287 | -5870.4159 | -5839.7875 | -5818.2656 | -5514.6821 | -4846.3021 | -5763.5882 | -5629.7064 | -5573.6761 | -2883.7074 | -4737.133 | -5020.3386 | -5438.0059 | -5630.3383 | -5428.4825 | -5350.7422 | -5780.4196 | -5319.3509 | -5307.1791 | -2809.7074 | -6066.6367 | -5234.3973 | -5240.8679 | -5203.5982 | -4539.4499 | -5137.5004 | -5325.7993
A6 | -8808.5099 | -8877.7781 | -8455.5371 | -8705.8086 | -7611.9642 | -7575.1222 | -7987.0445 | -8156.205 | -7509.7604 | -7301.8177 | -7259.0598 | -7554.1192 | -7688.7094 | -7056.6852 | -6906.6523 | -4386.6305 | -5127.2079 | -6927.9763 | -6743.5051 | -3803.1236 | -5183.7474 | -7142.08 | -5573.2027 | -5538.2396 | -6255.5069 | -6888.2363 | -6208.7722 | -6443.2414 | -5496.7772 | -3120.0249 | -6035.8072 | -6254.504 | -5018.967 | -6130.9296 | -6334.2094 | -6303.8476 | -5788.7212 | -5563.8919 | -6043.7288 | -5680.0541 | -5904.6858 | -2826.1683 | -5605.4767 | -5449.6237 | -5805.4336 | -5536.0571 | -5823.5059 | -5806.1836 | -5659.4509 | -5702.4095 | -5697.6029 | -2926.348 | -5277.1875 | -5243.9091 | -5672.1726 | -5723.2428 | -5142.1256 | -5430.014 | -5457.1274
E | -7845.5489 | -8074.0281 | -7207.2753 | -8209.2696 | -8022.5697 | -8043.7862 | -6593.4273 | -7945.1933 | -7916.6471 | -7517.595 | -7811.9816 | -6013.545 | -7655.2289 | -8017.9626 | -6863.9062 | -5118.7008 | -5076.1533 | -5743.4372 | -5975.5715 | -4687.9752 | -4163.4857 | -7463.2753 | -4103.0191 | -4937.0951 | -6260.4132 | -6373.4433 | -6790.1941 | -5862.2101 | -3547.7343 | -4340.2593 | -3921.7213 | -7137.3418 | -5038.6935 | -7050.2753 | -6338.8578 | -7406.5742 | -4320.5688 | -3611.47 | -5256.1702 | -5796.9291 | -6998.9143 | -3417.809 | -3447.9767 | -3398.1706 | -6668.8438 | -5592.0649 | -7063.2285 | -6760.9981 | -6571.4391 | -6491.4369 | -6715.6146 | -2906.4417 | -6775.1797 | -5280.0809 | -6955.7039 | -6984.0279 | -4234.5085 | -6448.4535 | -5931.4828
E1 | -8583.7482 | -8912.6296 | -8119.7753 | -8956.0703 | -8875.0697 | -8870.1847 | -7806.4273 | -8577.4941 | -8786.1471 | -8089.095 | -8775.9816 | -7008.9474 | -8248.8304 | -8114.4626 | -7865.1055 | -5939.8024 | -5728.7509 | -6480.5388 | -7079.6731 | -5832.8775 | -4346.4857 | -8146.7753 | -4401.1167 | -6022.0951 | -6390.1163 | -6162.6425 | -7114.8933 | -5812.5109 | -3949.8358 | -4943.5601 | -4330.7213 | -6401.6407 | -5658.7951 | -6374.8749 | -6057.8578 | -7779.4745 | -3984.3657 | -3744.5677 | -5585.1702 | -5769.8275 | -5972.7132 | -4381.9066 | -3715.2775 | -4627.073 | -6725.3438 | -6149.6664 | -7295.127 | -6354.5 | -5992.2399 | -5818.0345 | -6692.7162 | -3656.7386 | -7413.082 | -5190.3817 | -6197.7039 | -6250.3287 | -5104.9069 | -6471.2543 | -6291.8813
E2 | -7645.8458 | -7721.9265 | -7272.873 | -7617.0703 | -8450.2689 | -8269.6847 | -6965.1265 | -7249.9941 | -8299.4479 | -7891.095 | -8107.5832 | -6625.045 | -6759.0297 | -7769.7594 | -7401.1055 | -6908.1032 | -6766.6533 | -6250.0388 | -6574.7707 | -6605.8775 | -6593.7864 | -6302.3769 | -6476.1167 | -6432.7943 | -6960.0148 | -6310.9433 | -7711.991 | -5873.2101 | -6154.6366 | -6125.7593 | -4062.3229 | -6398.043 | -5963.1935 | -6348.1737 | -6157.6547 | -5728.2734 | -3977.9673 | -5772.1693 | -5223.8733 | -6152.7299 | -6323.9143 | -5565.6058 | -5504.6798 | -3629.073 | -6322.1446 | -4273.0649 | -5229.627 | -6238.7969 | -4816.3376 | -5983.9369 | -4802.015 | -5295.8402 | -7979.2812 | -5838.3817 | -6190.2039 | -6113.1256 | -4854.9069 | -4400.1547 | -5115.7836
E3 | -7923.0489 | -8300.3288 | -7749.2753 | -7972.1719 | -8341.8705 | -8314.1847 | -7094.8257 | -7988.2949 | -8555.8502 | -7586.8919 | -8164.6808 | -6487.8458 | -7472.4281 | -7563.2594 | -7318.8086 | -4584.904 | -5065.954 | -6522.8396 | -6560.5715 | -3941.4752 | -4102.5833 | -7613.7753 | -4177.1167 | -4625.4935 | -7420.3155 | -6506.1425 | -7530.6941 | -6272.3078 | -3693.9374 | -3794.2593 | -3358.4244 | -6882.3418 | -5091.8928 | -6977.3749 | -6413.557 | -6947.5742 | -3428.8657 | -3440.2669 | -5574.8733 | -6952.9291 | -6722.0139 | -3560.9066 | -3018.0783 | -2973.9714 | -6571.545 | -5433.2641 | -6544.2285 | -6521.0977 | -5322.9391 | -6104.8353 | -6407.6146 | -3177.6409 | -8303.2812 | -6613.3817 | -6794.907 | -6714.1256 | -4896.0085 | -6136.055 | -5035.7836
M | -8213.5177 | -8372.6296 | -7817.9082 | -8257.4883 | -8182.851 | -8141.1886 | -7360.2202 | -7930.8495 | -8105.8385 | -7621.9153 | -7896.0441 | -6821.8771 | -7487.2875 | -7603.2751 | -7211.3711 | -5281.5563 | -5509.1454 | -6446.9372 | -6601.8723 | -4832.608 | -4853.3724 | -7198.0136 | -4948.7964 | -5512.388 | -6570.7257 | -6412.9707 | -6947.3347 | -6076.6164 | -4625.6796 | -4302.5562 | -4568.0807 | -6517.0469 | -5308.4553 | -6458.6737 | -6190.2992 | -6663.9765 | -4502.5181 | -4496.4466 | -5574.5648 | -5997.0619 | -6249.3186 | -3772.7035 | -4338.1017 | -4183.0417 | -6255.2325 | -5435.7367 | -6230.709 | -6172.0625 | -5690.4548 | -5903.3353 | -5937.1107 | -3462.1019 | -6969.1211 | -5566.7489 | -6175.2859 | -6164.7467 | -4795.3092 | -5670.5668 | -5526.2914

## Slide 14: seven-day-ahead large load forecast errors (actual load - load forecast)
Chart: seven-day-ahead large load forecast errors (actual load - load forecast)
278 hours out of 6,552 hours when 7-d-ahead load forecast error > 6000 MW

## Slide 15: seven-day-ahead large load forecast errors (actual load - load forecast)
Chart: seven-day-ahead large load forecast errors (actual load - load forecast)
163 hours out of 6,552 hours when 7-d-ahead load forecast error < -4000 MW

## Slide 16: DA Peak Hour Model Results
The following slides show the day ahead peak demand accuracy for the last 3 summers (June – September) for the seven forecast models
  This is only a quantification of the results for the daily peak demand
Data is provided on a monthly aggregate basis and on a daily basis for 2019
Notes: This info on peak hour forecast accuracy was requested at last meeting
Tightest conditions may not just happen at peak, so accurate forecast for all hours is important

## Slide 17: Day Ahead – Daily Peak Forecast Performance
Chart: Summer of 2019
| Jun-19 | Jul-19 | Aug-19 | Sep-19
Active | 0.03 | 0.0182 | 0.0225 | 0.0239
A3 | 0.0386 | 0.0197 | 0.0326 | 0.03
A6 | 0.0445 | 0.0204 | 0.0372 | 0.0298
E | 0.0289 | 0.0158 | 0.0211 | 0.0224
E1 | 0.0309 | 0.0183 | 0.0234 | 0.0236
E2 | 0.0307 | 0.0217 | 0.0216 | 0.0239
E3 | 0.0288 | 0.0164 | 0.0211 | 0.0215
M | 0.0298 | 0.0162 | 0.0236 | 0.0233

## Slide 18: Day Ahead – Daily Peak Forecast Performance
Chart: Summer of 2018
| Jun-18 | Jul-18 | Aug-18 | Sep-18
Active | 0.0162 | 0.0184 | 0.0196 | 0.0351
A3 | 0.0172 | 0.0266 | 0.0229 | 0.0375
A6 | 0.0176 | 0.0251 | 0.0227 | 0.0346
E | 0.0164 | 0.0179 | 0.0195 | 0.0368
E1 | 0.0163 | 0.0186 | 0.0215 | 0.0332
E2 | 0.0164 | 0.0218 | 0.0196 | 0.0359
E3 | 0.0157 | 0.0165 | 0.018 | 0.0315
M | 0.0158 | 0.0195 | 0.0181 | 0.034

## Slide 19: Day Ahead – Daily Peak Forecast Performance
Chart: Summer of 2017
| Jun-17 | Jul-17 | Aug-17 | Sep-17
Active | 0.0265 | 0.0217 | 0.0289 | 0.016
A3 | 0.029 | 0.0224 | 0.0392 | 0.0251
A6 | 0.0269 | 0.0233 | 0.0392 | 0.0273
E | 0.0261 | 0.0203 | 0.0255 | 0.0176
E1 | 0.0291 | 0.0205 | 0.03 | 0.0213
E2 | 0.0279 | 0.0223 | 0.0306 | 0.0154
E3 | 0.0285 | 0.02 | 0.0303 | 0.0163
M | 0.0273 | 0.0197 | 0.0306 | 0.0175

## Slide 20: Day Ahead – Daily Peak Forecast Performance
Chart: June 2019 Day Ahead Daily Peak Demand Error
| 43617.708333333336 | 43618.75 | 43619.708333333336 | 43620.625 | 43621.708333333336 | 43622.708333333336 | 43623.708333333336 | 43624.75 | 43625.708333333336 | 43626.708333333336 | 43627.666666666664 | 43628.75 | 43629.75 | 43630.708333333336 | 43631.75 | 43632.625 | 43633.75 | 43634.75 | 43635.75 | 43636.75 | 43637.708333333336 | 43638.625 | 43639.75 | 43640.75 | 43641.708333333336 | 43642.708333333336 | 43643.708333333336 | 43644.666666666664 | 43645.708333333336 | 43646.75
Active | 1680 | -1444 | -971 | -2684 | 238 | 1008 | -901 | 773 | -7147 | 2324 | -1004 | -1357 | 2931 | 488 | -1570 | -5197 | -1516 | 166 | 797 | -1341 | 155 | -1116 | 2603 | -5805 | -2953 | -500 | -2462 | 1155 | -206 | 310
A3 | 2820 | -1627 | 273 | -3187 | -1713 | 889 | -2260 | 535 | -7783 | 1566 | -1064 | -961 | 2082 | -822 | -1570 | -7278 | -1516 | 74 | -1343 | -4008 | -2034 | -2407 | 2455 | -5689 | -3215 | -3191 | -4248 | 331 | -1054 | -378
A6 | 1818 | -3412 | -971 | -4017 | -960 | 2373 | -1165 | 1595 | -9022 | 1421 | -731 | -1158 | 2286 | -1818 | -2707 | -8054 | -1249 | -1007 | -3415 | -7056 | -2528 | -2865 | 2137 | -4744 | -1993 | -2834 | -3587 | 328 | -1295 | -1314
E | 1209 | -845 | 304 | -2684 | -1236 | 1008 | -901 | 773 | -7147 | 1855 | -1004 | -1357 | 1715 | 668 | 738 | -6074 | -1727 | -394 | 344 | -1283 | 531 | -1008 | 2030 | -6069 | -3185 | -500 | -1892 | 1132 | 470 | 310
E1 | 1586 | -1199 | 967 | -2203 | 297 | 1532 | -696 | 1520 | -6304 | 3294 | -991 | -1226 | 1857 | 1352 | 1254 | -4569 | -468 | 603 | 797 | -1627 | -60 | -609 | 2420 | -6325 | -3544 | -1664 | -2207 | 1155 | -420 | 1573
E2 | 1393 | -400 | 1417 | -2237 | 55 | 2456 | -458 | 722 | -7062 | 2324 | -188 | -235 | 3593 | 1236 | 1968 | -4635 | -107 | 1313 | 1304 | -1000 | 826 | -467 | 3770 | -4284 | -1202 | 2869 | 235 | 1859 | 3333 | 1847
E3 | 1253 | -1181 | 930 | -2533 | 238 | 1611 | -400 | 1206 | -6478 | 1994 | -999 | -1072 | 2931 | 488 | 403 | -5197 | -798 | 166 | 398 | -1341 | 155 | -1116 | 2603 | -5805 | -2953 | -1869 | -2462 | 670 | -206 | 1017
M | 1680 | -1444 | 487 | -2810 | -553 | 1645 | -980 | 1059 | -7299 | 2076 | -829 | -1001 | 2411 | 184 | 14 | -5968 | -978 | 126 | -319 | -2719 | -519 | -1412 | 2569 | -5486 | -2682 | -1198 | -2360 | 912 | 138 | 509

## Slide 21: Day Ahead – Daily Peak Forecast Performance
Chart: July 2019 Day Ahead Daily Peak Demand Error
| 43647.708333333336 | 43648.708333333336 | 43649.708333333336 | 43650.708333333336 | 43651.708333333336 | 43652.708333333336 | 43653.75 | 43654.666666666664 | 43655.75 | 43656.708333333336 | 43657.708333333336 | 43658.708333333336 | 43659.708333333336 | 43660.75 | 43661.708333333336 | 43662.666666666664 | 43663.708333333336 | 43664.708333333336 | 43665.708333333336 | 43666.708333333336 | 43667.75 | 43668.708333333336 | 43669.75 | 43670.75 | 43671.75 | 43672.708333333336 | 43673.75 | 43674.75 | 43675.666666666664 | 43676.708333333336 | 43677.708333333336
Active | 3428 | 1430 | -1917 | 775 | 1597 | -13 | 464 | 126 | -1209 | -1169 | 216 | -916 | -1932 | -251 | 1222 | 2501 | -328 | 542 | 1211 | 596 | -665 | -4139 | -782 | 359 | 212 | 992 | 2695 | 1082 | -2166 | 1623 | -285
A3 | 3221 | -40 | -1530 | -378 | 520 | -565 | 187 | 271 | -1567 | -2290 | -838 | -1234 | -3115 | -2397 | 2428 | 1704 | -328 | 311 | 1166 | 1267 | -665 | -4139 | -2850 | -1101 | -157 | -217 | 1645 | 484 | -1663 | 1348 | -196
A6 | 2642 | -798 | -1917 | -1387 | -670 | -783 | 444 | 85 | -2152 | -3366 | -521 | 572 | -1421 | -2451 | 2890 | 876 | -1672 | -483 | -154 | 674 | -253 | -4377 | -2291 | 257 | 539 | -654 | 1103 | 18 | -3586 | -478 | -1952
E | 3785 | 1511 | -435 | 398 | 2352 | 354 | 484 | 7 | -590 | -900 | -55 | -11 | -1207 | 478 | 1222 | 1591 | 283 | 542 | 1211 | 1257 | 580 | -3429 | -782 | 359 | 212 | 41 | 2552 | 1082 | -2166 | 1675 | 679
E1 | 3283 | 1976 | 823 | 404 | 1548 | 459 | 1052 | 725 | 233 | 28 | 415 | 54 | -1932 | -251 | 2553 | 2651 | 834 | 996 | 1182 | 1099 | 609 | -2467 | -19 | 1318 | 1409 | 1345 | 2830 | 1488 | -969 | 1784 | 427
E2 | 6871 | 2964 | 398 | 775 | 1258 | -13 | 1033 | 324 | -1209 | -1169 | -913 | -916 | -1577 | -233 | 2589 | 2728 | 1275 | 1026 | 1290 | 1746 | -148 | -2531 | -1011 | 392 | 974 | 849 | 3180 | 1698 | -594 | 1623 | -851
E3 | 3428 | 1430 | -592 | 327 | 1597 | -103 | 464 | 126 | -857 | -848 | 216 | 642 | -1331 | -200 | 2340 | 2501 | 291 | 504 | 1038 | 596 | -183 | -3131 | -2 | 1016 | 1386 | 992 | 2695 | 1110 | -807 | 2395 | 180
M | 3872 | 1174 | -542 | 23 | 1101 | -109 | 611 | 256 | -1024 | -1424 | -283 | -149 | -1764 | -842 | 2337 | 2008 | 114 | 483 | 956 | 1106 | -10 | -3346 | -1159 | 374 | 727 | 393 | 2334 | 980 | -1631 | 1391 | -285

## Slide 22: Day Ahead – Daily Peak Forecast Performance
Chart: August 2019 Day Ahead Daily Peak Demand Error
| 43678.708333333336 | 43679.708333333336 | 43680.708333333336 | 43681.75 | 43682.708333333336 | 43683.708333333336 | 43684.708333333336 | 43685.708333333336 | 43686.708333333336 | 43687.708333333336 | 43688.75 | 43689.708333333336 | 43690.666666666664 | 43691.708333333336 | 43692.708333333336 | 43693.708333333336 | 43694.708333333336 | 43695.75 | 43696.708333333336 | 43697.75 | 43698.708333333336 | 43699.708333333336 | 43700.666666666664 | 43701.666666666664 | 43702.75 | 43703.708333333336 | 43704.708333333336 | 43705.708333333336 | 43706.708333333336 | 43707.583333333336 | 43708.708333333336
Active | -1468 | -880 | -3373 | 558 | 3013 | 621 | -63 | -1315 | -393 | 232 | -101 | -541 | -1108 | 458 | -60 | 29 | -888 | 344 | 550 | -2375 | -622 | 50 | -3350 | -220 | -1763 | -463 | -9507 | 1520 | 2709 | -392 | -6702
A3 | -818 | -835 | -4652 | 95 | 3941 | 1298 | -29 | -2117 | -2222 | -325 | -827 | -2652 | -1985 | -656 | -766 | -1042 | -913 | -1108 | -285 | -2324 | -2136 | -1355 | -4433 | -2085 | -3031 | -439 | -11183 | 132 | 2426 | -1695 | -9007
A6 | -1176 | -1463 | -4278 | -686 | 3338 | 290 | -1123 | -2982 | -3060 | 212 | -1015 | -2923 | -2326 | -715 | 326 | -1429 | -894 | -1484 | -1338 | -2964 | -2469 | -1643 | -4542 | -2380 | -4142 | -1877 | -12410 | 419 | 2673 | -997 | -9361
E | -1085 | -880 | -4897 | 558 | 2672 | 621 | -316 | -1127 | -371 | 232 | 240 | -368 | 3 | -104 | -60 | 19 | -888 | 344 | 550 | -1040 | -588 | 50 | -2856 | 78 | -1186 | -463 | -9177 | 2284 | 2679 | -281 | -6398
E1 | -319 | -560 | -3008 | 1335 | 3771 | 1416 | 1217 | -1277 | -870 | -116 | 441 | -922 | -1074 | 458 | -431 | 29 | -147 | 445 | -105 | -2375 | -622 | -427 | -3654 | -394 | -1804 | 1336 | -9731 | 880 | 2608 | 2 | -6043
E2 | -1468 | -797 | -2906 | 856 | 3821 | 1143 | 285 | -797 | -53 | -542 | -705 | -1013 | -813 | 155 | -397 | -302 | -232 | 691 | 1017 | -1265 | -692 | -31 | -2752 | 119 | -1147 | 313 | -8803 | 2158 | 3179 | 103 | -5665
E3 | -623 | -1058 | -3373 | 724 | 3013 | 1020 | -63 | -1315 | -393 | -829 | -101 | -541 | -456 | 565 | 244 | 439 | -473 | 424 | 1173 | -533 | -232 | 67 | -3056 | -220 | -1651 | 286 | -8640 | 2145 | 2650 | -87 | -6396
M | -915 | -932 | -3852 | 480 | 3426 | 965 | -5 | -1603 | -1161 | -228 | -328 | -1403 | -1108 | -50 | -181 | -381 | -591 | -114 | 169 | -1750 | -1123 | -556 | -3350 | -500 | -1763 | 207 | -9507 | 1520 | 2709 | -392 | -6702

## Slide 23: Day Ahead – Daily Peak Forecast Performance
Chart: September 2019 Day Ahead Daily Peak Demand Error
| 43709.708333333336 | 43710.708333333336 | 43711.708333333336 | 43712.708333333336 | 43713.708333333336 | 43714.708333333336 | 43715.708333333336 | 43716.708333333336 | 43717.708333333336 | 43718.708333333336 | 43719.666666666664 | 43720.708333333336 | 43721.708333333336 | 43722.708333333336 | 43723.708333333336 | 43724.708333333336 | 43725.708333333336 | 43726.708333333336 | 43727.666666666664 | 43728.666666666664 | 43729.708333333336 | 43730.708333333336 | 43731.708333333336 | 43733.708333333336 | 43734.708333333336
Active | -555 | 911 | 614 | -1455 | -2825 | -1495 | 570 | 956 | 748 | -2037 | -1384 | -992 | -2291 | -502 | 169 | -1372 | -3122 | 2560 | -5070 | 1853 | 2509 | 759 | 871 | 2060 | -141
A3 | -1756 | -559 | -839 | -3392 | -4743 | -3905 | -1369 | 1753 | 2012 | -1861 | -1767 | -1516 | -2280 | -1964 | -362 | -1758 | -3968 | 636 | -5460 | 864 | 1203 | -340 | 1758 | 1577 | -671
A6 | -1787 | -174 | -410 | -3292 | -4862 | -4064 | -1103 | 1789 | 1615 | -2495 | -2519 | -2239 | -2856 | -1668 | -432 | -2123 | -4395 | 694 | -5209 | 305 | 274 | -383 | 990 | 1143 | -1188
E | -605 | 1229 | 1003 | -602 | -2252 | -1818 | 570 | 1400 | 438 | -2165 | -1567 | -1430 | -1430 | -502 | -37 | -1366 | -3584 | 950 | -5070 | 1493 | 2485 | 542 | 871 | 2011 | -76
E1 | 55 | 1429 | 1402 | -910 | -2120 | -1495 | 761 | 956 | 748 | -1756 | -1689 | -1299 | -2291 | -981 | 169 | -1127 | -2906 | 1570 | -5675 | 1342 | 2649 | 721 | 874 | 2282 | -210
E2 | -115 | 274 | -502 | -2536 | -3606 | -2980 | -198 | 1382 | 1850 | -529 | -411 | 20 | -1287 | -171 | -866 | -1890 | -2865 | 2560 | -3759 | 3044 | 2657 | 1060 | 1606 | 1868 | -190
E3 | -357 | 2182 | 2003 | 163 | -1405 | -849 | 861 | 967 | 385 | -2037 | -1486 | -737 | -1267 | 213 | 771 | -718 | -3131 | 1516 | -5116 | 1531 | 2245 | 716 | 1112 | 2080 | -88
M | -555 | 911 | 614 | -1455 | -2825 | -2209 | 125 | 1292 | 1087 | -1670 | -1384 | -992 | -1711 | -681 | -65 | -1372 | -3122 | 1649 | -4905 | 1853 | 2509 | 759 | 1116 | 2060 | -141

## Slide 24: Day Ahead – Daily Peak Forecast Performance
Chart: 2019 Summer
| Active | A3 | A6 | E | E1 | E2 | E3 | M
Average Over Forecast | 1790.0159 | 2143.4286 | 2443.5349 | 1780.1754 | 1847.8462 | 1478.0172 | 1630.8182 | 1657.4559
Percent | 0.53846 | 0.71795 | 0.73504 | 0.48718 | 0.44444 | 0.49573 | 0.47009 | 0.5812
Chart: 2018 Summer
| Active | A3 | A6 | E | E1 | E2 | E3 | M
Average Over Forecast | 1565.8429 | 1816.6379 | 1787.6667 | 1556.0909 | 1429.7297 | 1666.6757 | 1380.3273 | 1441.2836
Percent | 0.57377 | 0.47541 | 0.46721 | 0.54098 | 0.60656 | 0.60656 | 0.45082 | 0.54918
Chart: 2017 Summer
| Active | A3 | A6 | E | E1 | E2 | E3 | M
Average Over Forecast | 1589.9867 | 1876.8413 | 1951.3871 | 1613.569 | 1693.2745 | 1803.3462 | 1600.3205 | 1749.3509
Percent | 0.61475 | 0.51639 | 0.5082 | 0.47541 | 0.41803 | 0.42623 | 0.63934 | 0.46721
Chart: 2017 - 2019 Summer Months
| Active | A3 | A6 | E | E1 | E2 | E3 | M
Average Over Forecast | 1642.4471 | 1969.0439 | 2112.3268 | 1645.0773 | 1628.5028 | 1645.8315 | 1544.883 | 1609.3021
Percent | 0.57618 | 0.56787 | 0.56787 | 0.50139 | 0.4903 | 0.5097 | 0.52078 | 0.53186

## Slide 25
Appendix

## Slide 26: MTLF Models
7 models are currently available
  5 are internally developed
  Named E, E1, E2, E3, and M
  2 are legacy “black box” models from GE
  Named A3 and A6

## Slide 27: MTLF Models
A3 Notes
  Uses recent history to update the model coefficients
  Prone to significantly over-forecast summer demands on very hot days
  Prone to significantly over-forecast winter demands on very cold days

## Slide 28: MTLF Models
A6 Notes
  Uses recent history to update the model coefficients
  Only uses one weather station per weather zone
  Prone to significantly over-forecast summer demands on very hot days
  Prone to significantly over-forecast winter demands on very cold days

## Slide 29: MTLF Models
E Notes
  Considered to be the overall best model for Day Ahead
  Slow to change during shorter forecast horizons (1 – 4 hours ahead)
  Calibrated based on most recent historical days (look back at the last 7 – 14 days)
  Tuned based on forecast performance during the current day (look back at the last 3 hours)

## Slide 30: MTLF Models
E1 Notes
  Designed to be the most responsive model to changing conditions
  Designed to perform well on very hot and very cold days
  Does not do well on mild days
  Can result in a jagged forecast shape
  Tuned based on forecast performance from the last hour

## Slide 31: MTLF Models
E2 Notes
  Looks more at rain and cloud cover
  More reliant on the weather forecast for the next 14 hours
  Best at capturing Winter/Spring/Fall rain type and cloud cover patterns
  Tendency to under forecast very hot conditions
  Calibrated based on most recent historical days (look back at the last 7 – 14 days)
  Tuned based on forecast performance during the current day (look back at the last 3 hours)

## Slide 32: MTLF Models
E3 Notes
  Provides more weight on weather for shorter term forecasts
  Relatively slow to change
  Input from additional weather stations
  Calibrated based on most recent historical days (look back at the last 7 – 14 days)
  Tuned based on forecast performance during the current day (look back at the last 3 hours)

## Slide 33: MTLF Models
M Notes
  The average of the 6 other models
  Historically has shown to be the best Day Ahead forecast
  Provides a good benchmark for other models