## Slide 1
Potential Price Correction:
Modeling of Withdrawn Outages in the Day-Ahead Market and Reliability Unit Commitment
Kenan Ögelman
Vice President – Commercial Operations
TAC
October 23, 2019

## Slide 2: Background
May 30, 2019 – Market Management System (MMS) system enhancement for modeling Outages in the Day-Ahead Market (DAM) and Reliability Unit Commitment (RUC)
  Enhancement intended to only model withdrawn Outages in DAM and RUC where out-of-service equipment was under restoration
  Software Implementation Error - MMS inadvertently modeled all withdrawn Outages for DAM and RUC; not just those undergoing restoration.
    Outages withdrawn before their planned outage start date were erroneously modeled in the DAM as out-of-service—i.e., some in-service Transmission Elements were identified as out-of-service in ERCOT’s network model when clearing the DAM.
  Prior to this system enhancement/software implementation error, when a transmission Outage status was withdrawn, the Outage would not be included in DAM and RUC models; DAM and RUC would not see the Outage.
September 24, 2019 – ERCOT became aware of the software implementation error and began investigating prices for Operating Days (ODs) May 30, 2019 through September 25, 2019.
September 25, 2019 – Emergency patch placed into production for OD September 26, 2019
October 3, 2019 – ERCOT issued Market Notice M-A100319-01
October 9, 2019 – ERCOT issued Market Notice M-A100319-02

## Slide 3: Background
Example - Pre-System Enhancement:
Example – Post-System Enhancement:
EQUIPMENT NAME | PLANNED START DATE | PLANNED END DATE | ACTUAL START DATE | ACTUAL END DATE | STATUS | DAM/RUC Model for 9/2
ABCD_A | 9/1/2019 10:00 | 12/11/2019 12:00 |  |  | Withd | Included
ABCD_B | 9/1/2019 10:00 | 12/11/2019 12:00 | 9/1/2019 22:04 |  | Withd | Included
ABCD_C | 9/1/2019 10:00 | 12/11/2019 12:00 | 9/1/2019 22:04 | 9/1/2019 22:04 | Withd | Not Included
Intended change
Unintended error

## Slide 4: Impacts
Market Impact: DAM & RUC
  No impact to the Real-Time Market (RTM)
  RUC models impacted, but no RUC instructions associated with transmission congestion or other system conditions that may have arisen out of this issue
Pricing Impact
  ERCOT identified erroneously modeled Outages in DAM and RUC for the following ODs: August 20 – 21, 2019 and September 16 – 25, 2019.
    ODs 08/20/19 & 08/21/19 – No Price Correction
      ERCOT determined that these ODs were affected by the system implementation error, but could not be corrected by ERCOT or authorized by the Board, as prices for these ODs were final, and outside the timeline for Board review. See Protocol Section 4.5.3(5)(a).
    ODs 09/16/19 – 09/23/19 – Board Review (December 2019)
    DAM clearing impacted for these ODs; ERCOT seeking Board review of the following prices: Day-Ahead Settlement Point Prices (DASPPs);DAM Market Clearing Prices for Capacity (MCPCs); and DAM Locational Marginal Prices (LMPs) for Electrical Buses.
    ODs 09/24/19 & 09/25/19 – ERCOT Price Correction
      ERCOT corrected prices for these ODs, before prices were final, in accordance with Protocol Section 4.5.3(4).

## Slide 5: Price Correction (Board Review)
Market: DAM
ODs: 09/16/19 – 09/23/19
ERCOT reran DAM with correct model inputs—i.e., Outages that had been withdrawn before their planned Outage start date were identified as in-service.
The following slide includes a summary of ERCOT’s preliminary study; this data is subject to change. Final data and detailed study results will be included in Board materials prior to the December meeting.

## Slide 6: Price Correction (Board Review) Summary of Price Impacts
* For 6/10/19 and 6/11/19, only the RUC model was affected. The DAM model was not impacted on those two days.
** For 9/24/19 and 9/25/19, corrected DAM prices were posted prior to becoming final.
OD | Number of Impacted Transmission Lines/ Transformers | Count of Changes in Price for the 4 Hubs and 4 Competitive Load Zones across All Hours of the Affected ODs |  |  |  |  |  | 
 |  | < -$10/MWh | >= -$10/MWh & < -$1/MWh | >= -$1/MWh & < -$0.1/MWh | >= -$0.1/MWh & < $0.1/MWh | >= $0.1/MWh & < $1/MWh | >= $1/MWh & < $10/MWh | >= $10/MWh
06/10/19 * | 2 | No Price Correction |  |  |  |  |  | 
06/11/19 * | 2 | No Price Correction |  |  |  |  |  | 
8/20/19 | 1 | No Price Correction |  |  |  |  |  | 
8/21/19 | 1 | No Price Correction |  |  |  |  |  | 
9/16/19 | 5 | 1 | 24 | 67 | 34 | 38 | 28 | 0
9/17/19 | 3 | 0 | 3 | 29 | 64 | 88 | 8 | 0
9/18/19 | 2 | 0 | 2 | 67 | 52 | 7 | 55 | 9
9/19/19 | 1 | 0 | 6 | 32 | 47 | 83 | 24 | 0
9/20/19 | 1 | 0 | 6 | 44 | 117 | 25 | 0 | 0
9/21/19 | 1 | 0 | 2 | 58 | 90 | 25 | 17 | 0
9/22/19 | 1 | 0 | 2 | 12 | 137 | 39 | 2 | 0
9/23/19 | 5 | 0 | 1 | 28 | 102 | 30 | 29 | 2
9/24/19 ** | 5 | 0 | 3 | 24 | 146 | 15 | 4 | 0
9/25/19 ** | 5 | 23 | 31 | 47 | 49 | 22 | 12 | 8
Note: a positive value indicates that the corrected or proposed price is higher than the original price.