## Help
HELP |  |  | COLLECTOR SYSTEM TEMPLATE
Template Version |  | V1k, 10/21/2019
Revisions:
| V1f | Creation, 10/5/2019
| V1k | Improved warning messages
Scroll down
Steps
1. Fill out this template Start from the Home page.
3. Save this template. Include your Site Code in the file name.
4. Upload to ERCOT via the RIOO-RS portal: ü This Template ü Your collector online ü Raw & Sequence file or Aspen file
5. Done!
Be sure to enable Macros in Excel!!
Examples - Filling Out
Two Resources, 1 Collector System
Two Resources, 2 Collector Systems
Mixed Resources, 2 Collector Systems
2. Run validations Buttons on the Home page.
The illustration at right is considered a single collector system because the two resources share a medium voltage station bus "SUB". The Segments sheet indicates which resource each segment is sharing.
Because there is only one collector "Island", both Resources are assigned to Island 1 on the Home sheet.
Each Resource is assigned to its Island on the Home sheet. Note: The ordering of islands is assigned by the spreadsheet automatically during validation. Check the validation message boxes to ensure you know the assigned ordering.
This example illustrates a Site with two collector systems, "two islands" because each collector system has its own station bus "SUB1" and "SUB2".
Each Resource is assigned to its Island. Resources 2 and 3 are both located on Island #2.
This situation often occurs when a site contains a mixture of turbines and the turbines must be represented as separate units. In this situation, a collector system ("Island") may contain a mixture of turbines.

## Home
HOME PAGE | COLLECTOR SYSTEM FORM
<Enter Site Code>
| NAME of UNIT RESOURCE--> | UNIT.1 | UNIT.2 | UNIT.3 | UNIT.4 | UNIT.5 | UNIT.6 | UNIT.7 | UNIT.8
Enter Model Name (e.g. GE2.7, etc)-->
Enter number of turbines / inverters-->
Enter total MW this Resource-->
| (Auto-Populated GenCode) | SITE_UNIT.1 | SITE_UNIT.2 | SITE_UNIT.3 | SITE_UNIT.4 | SITE_UNIT.5 | SITE_UNIT.6 | SITE_UNIT.7 | SITE_UNIT.8
| Resource Name (Auto Filled from Row 5 Above) | UNIT.1: Make Selection Here!
Unit1 |  | UNIT.1: (Make Selection)
Unit2 |  | UNIT.1: (Make Selection)
Unit3 |  | UNIT.1: (Make Selection)
Unit4 |  | UNIT.1: (Make Selection)
Unit5 |  | UNIT.1: (Make Selection)
Unit6 |  | UNIT.1: (Make Selection)
Unit7 |  | UNIT.1: (Make Selection)
Unit8 |  | UNIT.1: (Make Selection)
Note on B4: ERCOT: Ensure that the Site Code matches the officiall registration at http://www.ercot.com/gridinfo/generation/Resource_Site_Name_to_Mnemonic_Dictionary.xls For new (unregistered) resources, enter a short abbreviation for the site.
DATA
1.
Enter Resource Site Code and Unit Names exactly as registered.
2.
Enter Wind Turbine data and protection data.
4.
Enter basic descriptions.
ATTACHMENTS
PPS/e Version 33, 34 stability models must be provided (.dll file and model manual). Please zip your files prior to attaching.
5.
Excel 2011
Excel 2013
AUXILIARY DEVICES
6.
NOTES and VALIDATION
Click button to check form. Review incomplete warnings. Some warnings may be ignored if considered reasonable exceptions. Use the Notes field to document and track any changes. Per NERC, you are required to complete a MOD-026/27 review after a model change. A date field is provided here to help coordinate.
7.
SUBMIT
8.
Submit this form by first saving the file and then uploading the form. IT IS NO LONGER NECESSARY TO EMBED THIS FILE INTO YOUR RARF. Simply rename this file to include your site code or project name and then upload this file through the usual submission means (via RIOO for interconnection projects and VIA the RARF Service Request for comissioning / online generators).
Submit template to ERCOT. If also performing a NERC MOD-026 / 027 review, submit to your TSP.
For TSP / ERCOT Use
For TSP / ERCOT Use
9.
This section has buttons to download the finished .dyr model file. (Generally for TSP / ERCOT use.)
ERCOT / TSP Use
Fill out bus table below and click to get a .dyr file with the bus numbers.
1. First, click on the upload space at right.
2. Next, open the Insert Object dialog in Excel: In Excel 2011, click Insert -> Object In Excel 2013, click Insert -> Pulldown button -> Object
3. Select "From File". Browse to get the zipfile, then click "Display as Icon."
In order to fully represent your plant capability, ERCOT would like to understand how auxiliary devices are controlled, such as STATCOMS, DVARs, and switched shunts.
Provide models for any auxiliary dynamic devices such as STATCOMs and DVARs. Attach .dll files and model manuals to the Attachments box and paste .dyr info at right.
Use the box at right to provide any additional .DYR models. Where bus numbers and unit IDs are required, please substitute in the following tags: <RESOURCE_NAME:BUS> to represent the generator bus <RESOURCE_NAME:MVBUS> to represent the 34.5 kV bus <RESOURCE_NAME:ID> to represent the unit id <RESOURCE_NAME:POI> to represent the POI bus <RESOURCE_NAME:MINS> to represent aux (non-bus) models where "RESOURCE_NAME" is replaced by one of the names in ROW 12.
Please zip the files before attaching.
To select a model: First click on the words "(Make Selection)". A pull-down button will appear. Click and select your model.
3.
Enter Cable Data.
Enter cable data. Impedances are per-unit per 1000 ft of cable. The per-unit base is 100 MVA at the voltage which the cable operates. If the same cable is used at multiple resources (units), then the user may opt to only enter that cable type once.
4.
Enter Segment Data.
Enter segment data. User should enter node names in the From and To columns. Cables which share a node are considered electrically connected. The node names can be any alphanumeric identifier. Please be cautious about misspellings, as this will cause an electrical disconnect. The "Number of Turbines on Segment" refers to the number of downstream turbines that segment feeds, either directly or indirectly. For plants where each resource has its own collector system, simply designate a Resource for each collector branch. For plants where multiple Resources share a collector branch, select "(Multiple)" in the Resource column.
5.
Fetch Data.
(Click Validate! button.)
To begin the consistency check, first fetch the worksheet data into memory. Error messages will be printed to the right.
VALIDATION
(Click button to Load Data.)
7.
Provide names of Origin Nodes.
Please enter the names of the Origin Nodes in the textbox below. Origin Nodes generally represent medium voltage Substation buses; these are the nodes from which the collector system branches outward. The names should match either a From or a To node name in the Segments worksheet. **Important: Exactly ONE origin node should be provided for EACH island.** Once done, click Check.
8.
Validate!
6.
Check for Collector Islands.
Each disjoint collector system forms an island. Some projects have multiple collector systems (islands) with each collector system having its own MPT (main power transformer). Islands can also be created accidentally when a segment is missing or misspellings in the From/To Node Names. Click Check Islands to get a summary for review. Generally, there should be one island per medium voltage station bus. The order of Islands does not matter. Refer to the Help sheet for example illustrations of different types of collector systems.
(Click Check Islands.)
5.
Enter Node Data. (Filling out this sheet is only required in certain circumstances. See notes at right.)
The Node Data sheet is required if your collector system contains a mix of resources and therefore you enter the word '(Multiple)' in the Segment sheet Resource Column.
7.
Confirm the Resources associated with each Island.
Please confirm associations below. Each isolated collector system "Island" may serve one or more Resources. Select an island for each Resource using the pull-down menus in the yellow box below. If the resource name is blank, this is because you left a default name in Row 5.
(Click Check Islands button above to populate this help box.)
Helpful Hints (Auto-Populated)
(Click Check Associations.)
If there are more islands than expected, ensure there are no disconnects in the Segments sheet and that each collector system fully connects all the way back to the common Substation Bus(es). Any data errors will likely occur near one of the Nodes listed to the right. If the number of turbines is incorrect, check the numbering in Column H on the Segments worksheet. Each segment should be assigned a number corresponding to the number of turbines supported by that segment (how many turbines or inverters send their power through that segment).
(Enter names of origin nodes here separated by commas.)
VALIDATION
<-- Click to check the associations you entered in the yellow box. Warning messages will appear below.
Note: You cannot leave the default name as "UNIT.1", etc. You must change the name to match your registered name. If your resource is new, pick another name such as W1, etc.
Example: Segment E-F is missing, incorrectly causing creation of a second island.
Validation Error Messages
Topology Check (# Turbines each Node)

## Cable_Data
<-- Return to Home page | CABLE DATA
GENERATOR DETAILS | COLLECTION SYSTEM DETAILED MODEL |  | POSITIVE SEQUENCE DATA |  |  | ZERO SEQUENCE DATA
Resource Name | Cable Type | Voltage Level kV | R/kft | X/kft | Charging Bc/kft | R0/kft | X0/kft |  | Internal Use / Don't Edit
(Resource Name is Optional Here) | (Name Must Be Unique) | kV | (p.u. on 100 MVA base) | (p.u. on 100 MVA base) | (p.u. on 100 MVA base) | (p.u. on 100 MVA base) | (p.u. on 100 MVA base) | Resources
(Unassociated)
SITE_UNIT.1
SITE_UNIT.2
SITE_UNIT.3
SITE_UNIT.4
SITE_UNIT.5
SITE_UNIT.6
SITE_UNIT.7
SITE_UNIT.8
Note on A4: ERCOT: In previous versions of the RARF, cables needed to be associated with a specific Resource. This is no longer necessary. If multiple Resources use the same cables then the cable definition can be entered once.
Define the cable types being used here. Impedances are per-unit per 1000 ft of cable. The per-unit base is 100 MVA at the voltage which the cable operates. If the same cable is used at multiple resources (units), then you may opt to only enter the cable type once and leave the Resource column blank.

## Segments
<-- Return to Home page | SEGMENT DATA
GENERATOR DETAILS | Cable Type | RENEWABLE SEGMENT DETAILS
Resource Name (Unit Code/Mnemonic) | Cable Type | From Node | To Node | Circuit Number | Voltage Level | Cable Segment Length | Number of Turbines/Inverters On Cable Segment | Internal Use / Don't Edit (Below is Mirrored from Cable_Data sheet)
List | List | alpha/numeric | alpha/numeric | alpha/numeric | kV | in kft | Integer | Cables | Resources
(Mixed)
SITE_UNIT.1
SITE_UNIT.2
SITE_UNIT.3
SITE_UNIT.4
SITE_UNIT.5
SITE_UNIT.6
SITE_UNIT.7
SITE_UNIT.8
Note on A3: Concatenated mnemonic of Resource Site Code and Unit name (e.g.. CBY_CBYG1) from http://www.ercot.com/gridinfo/generation/Resource_Site_Name_to_Mnemonic_Dictionary.xls
Note on H3: ERCOT: Enter the number of turbines whose power this segment is intended to carry. Segments near the station will carry most--if not all--of the turbines. Far segments will carry power from only one turbine or inveter.
Note on H4: ERCOT: Enter the number of turbines whose power this segment is intended to carry. Segments near the station will carry most--if not all--of the turbines. Far segments will carry power from only one turbine or inveter.
Note on G4: ERCOT: kft = 1000 feet
Note on E4: Optional, enter a very short number or name for this segment:
Note on C3: ERCOT: Enter a unique name for this node.
Note on D3: ERCOT: Enter a unique name for this node.
Example Collector System: 4 Turbines
Column H should indicate how many turbines each segment supports.
Define the connections between turbines/inverters here. Connections are made by naming the from / to nodes. The Resource Name column should indicate which downstream Resources are being fed by each segment. (See the Help worksheet for illustrations.) An example of how to fill in Column H is illustrated below.

## Output_csv
// !----------------------------- Output CSV -- DO NOT EDIT -----------------------------------/
// (Refresh by clicking Refresh button.)