## Slide 1
FIS Dynamic Study Approach
October 28, 2019

## Slide 2: Background
In QSA process, several issues in the FIS stability study reports were identified. If not performed appropriately:
  False stability issues may show up, mainly because existing GTCs were not respected;
  Real stability issues may not be captured, mainly because appropriate cases and dispatches were not used.
System improvements or mitigation plans:
  PG 5.9 requires that system improvements or mitigation plans need to be identified in the FIS stability study for a GINR to be qualified for QSA.

## Slide 3: Respecting Existing GTCs
Existing GTC definitions are available on ERCOT MIS:
https://mis.ercot.com/pps/tibco/mis/Pages/Grid+Information/Transmission
Project falls inside a GTC, two scenarios to be studied:
  Scenario 1: The project dispatched at Pmax; Existing generators inside the GTC dispatched at the same level such that their total output equals to the GTL;
  Scenario 2: All generators, including the studied project, dispatched at the same level such that the total output of all generators inside the GTC equals to the GTL;
  No need to study scenarios 2 if system performance acceptable in scenario 1.

## Slide 4: Respecting Existing GTCs
Project falls outside, but electrically close to, a GTC:
  The studied project dispatched at Pmax;
  Existing generators inside the GTC dispatched at the same level such that their total output equals to the GTL;
If the GTL for the base case (N-0) is not defined, all generators inside the GTC should be dispatched at Pmax.
For system conditions with pre-outages (P6 events):
  If GTC is defined for the studied outage, it should be respected;
  If GTL is not defined for the studied outage, the GTL for the base case (N-0) condition should be respected.

## Slide 5: Respecting Existing GTCs
Panhandle GTC:
  Panhandle GTC should be treated in the same way as all other GTCs, as discussed in previous slides;
  For a specific system condition, the minimum between the WSCR, VSAT, and Dynamic Stability Limits should be respected.
Future system conditions:
  The existing GTCs are defined for current and near-term system conditions;
  If a GTC is no longer valid for the system conditions of the targeting COD due to system changes, disregard the GTC.

## Slide 6: Mitigation Plans
Curtailment as a mitigation plan is suggested to be identified in the following approach:
  If the project is not inside or electrically close to a GTC, curtail the project until a stable system response is achieved; Nearby generators remain at Pmax;
  If the project falls inside a GTC, both the project and existing generators inside the GTC should be curtailed until a stable system response is achieved;
  If the project falls outside, but electrically close to, a GTC, keep the dispatch of generators inside the GTC the same, curtail the project until a stable system response is achieved.

## Slide 7: Study Cases and Dispatch
By default, both HWLL and summer peak cases should be studied for any generation projects.
If one of them will not be studied, TSPs need to provide the rationale in the FIS study scope agreement and get reviewed/agreed by ERCOT.
By default, dynamic load models should be used in the study. If not, the reason should be included in the study reports.

## Slide 8: Study Cases and Dispatch
For renewable projects in weak regions like Panhandle, West, Far West, and Valley:
  HWLL case is suggested to be used;
  All nearby wind and solar generators should be in-service and dispatched at Pmax, if not limited by a GTC.
  If there are conventional generators nearby the project, two scenarios are suggested to be studied:
    All conventional generators dispatched at Pmax, if not limited by a GTC;
    All conventional generators turned off;
    If one of the them not studies, the rationale needs to be included in the FIS study report.
.

## Slide 9: Energy Storage Study Scenarios
Storage only, two scenarios to be studied:
  Charging mode
  Discharging mode
PV or Wind + storage, three scenarios to be studied:
  PV or Wind + storage in discharging mode
  PV or Wind only
  Storage in charging mode
Study approach for storage will be adjusted/improved as our experience grows.