## Slide 1
PDCWG Report to ROS
Chair: Chad Mulholland, NRG
Vice Chair: Jimmy Jackson, CPS
ROS
November 7th, 2019

## Slide 2: Report Overview & Notes
Report Overview
  Meeting Minutes
  BAL-001-TRE-1 FMEs & IMFR
    3 FMEs in the month of September
  Frequency Control Report

## Slide 3: Meeting Minutes
PDCWG Meeting 10/9/19
  Southern Cross DC Tie – Directive 3, DC Tie Ramping Limits
    Discuss Protocol Changes (Curtailment option)
  ERCOT Ancillary Service Analysis – Changes for 2020
    New NPRR 968 to increase MSSC from 1,375 MW to 1,430 MW
  Energy Dispatch Performance Monitoring for Energy Storage Devices
    (NPRR 963)
  SAR-12 (Standard Authorization Request), BAL-001-TRE
  ERCOT Governor Testing Requirements
    (Nodal Operating Guide 2.2.7 clarification – NDCRC Submissions)
  Regulation & Frequency Control Reports

## Slide 4: Frequency Measurable Events Performance

## Slide 5: Frequency Measurable Events
There were 3 FMEs in September
  9/21/2019 03:00:17
    Loss of 462 MW
    Interconnection Frequency Response: 1,215 MW/0.1 Hz
    9 of 48 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    4 of 48 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.
  9/22/2019 14:49:57
    Loss of 697 MW
    Interconnection Frequency Response: 1,244 MW/0.1 Hz
    6 of 37 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    6 of 37 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 6: Frequency Measurable Events
  9/22/2019 15:27:34
    Loss of 418 MW
    Interconnection Frequency Response: 747 MW/0.1 Hz
    8 of 41 Evaluated Generation Resources had less than 75% of their expected Initial Primary Frequency Response.
    8 of 41 Evaluated Generation Resources had less than 75% of their expected Sustained Primary Frequency Response.

## Slide 7: Interconnection Minimum Frequency Response (IMFR) Performance
IMFR Performance currently 1254.21 MW/0.1Hz
Frequency Response Obligation (FRO): 381 MW/0.1 Hz

## Slide 8: Frequency Control Report
September 2019

## Slide 9: CPS1 Performance

## Slide 10: RMS1 Performance of ERCOT Frequency

## Slide 11: Frequency Profile Analysis

## Slide 12: Time Error Corrections

## Slide 13: ERCOT Total Energy

## Slide 14: ERCOT Total Energy from Wind Generation

## Slide 15: ERCOT % Energy from Wind Generation

## Slide 16: ERCOT Total Energy from Solar Generation

## Slide 17: ERCOT % Energy from Solar Generation

## Slide 18
Questions?