ERCOT Nodal Operating Guides

Section 4:  Emergency Operation

November 1, 2019

4	EMERGENCY OPERATIONS	4-2

4.1	Introduction	4-2

4.2	Communication Under Emergency Conditions	4-2

4.2.1	Operating Condition Notice	4-2

4.2.2	Advisory	4-3

4.2.3	Watch	4-5

4.2.4	Emergency Notice	4-6

4.3	Operation to Maintain Transmission System Security	4-7

4.3.1	Real-Time and Short Term Planning	4-7

4.4	Block Load Transfers between ERCOT and Non-ERCOT System	4-7

4.5	Energy Emergency Alert (EEA)	4-8

4.5.1	General	4-8

4.5.2	Operating Procedures	4-8

4.5.3	Implementation	4-10

4.5.3.1 	General Procedures Prior to EEA Operations	4-12

4.5.3.2	General Procedures During EEA Operations	4-13

4.5.3.3	EEA Levels	4-14

4.5.3.4	Load Shed Obligation	4-20

4.5.3.5	EEA Termination	4-20

4.6	Black Start Service	4-21

4.6.1	Principles	4-21

4.6.2	Strategies	4-22

4.6.3	Priorities	4-23

4.6.4	Responsibilities	4-23

4.6.5	Black Start Emergency Back Up Communication Facilities Criteria	4-27

4.7       Geomagnetic Disturbance Operating Plan	4-27

4.7.1	Monitoring and Dissemination of Space Weather Information	4-27

4.7.2	Development and Submission of TO GMD Operating Procedures or Processes	4-27

4.7.3	ERCOT’s GMD Operating Plan and ERCOT Review of TO GMD Operating Procedures or Processes	4-28

4.8	Responsive Reserve Service During Scarcity Conditions	4-29

4.8.1	Responsive Reserve Service Manual Deployment	4-29

4.8.2	Responsive Reserve Service Manual Recall	4-30

# EMERGENCY OPERATIONS

4.1	Introduction

(1)	Emergency operation is intended to address operating conditions under which the reliability of the ERCOT System is inadequate and there is no solution readily apparent.  During a declared system emergency, ERCOT can instruct Transmission Operators (TOs) and Qualified Scheduling Entities (QSEs) to take specific operating actions that would otherwise be discretionary.  Upon receiving a Verbal Dispatch Instruction (VDI) from ERCOT, and in compliance with these Operating Guides, the QSEs shall direct relevant Resources or groups of Resources to respond to the instruction.  ERCOT shall coordinate with QSEs and TOs to assure that necessary actions are taken to maintain reliability.

(2)	It is essential that good, timely, and accurate communication routinely occur between ERCOT, TOs, and QSEs.  QSE and TO personnel shall report unplanned equipment status changes as outlined in this Section.  ERCOT System Operators may ask for status updates as required in order to gather information to make decisions on system conditions to determine what type of emergency communication may be appropriate.

(3)	ERCOT may issue communications in the form of Operating Condition Notices (OCNs), Advisories, Watches and Emergency Notices.  These communications may relate to but are not limited to, weather, transmission, computer failure, or generation information.  ERCOT shall specify the severity of the situation, the area affected, the areas potentially affected, and the anticipated duration of the Emergency Condition.  These communications will be issued by ERCOT to inform all TOs and QSEs of the current operating situation.  TOs will notify their represented Transmission Service Providers (TSPs) and Load Serving Entities (LSEs).  QSEs will in turn notify the appropriate Resources, Retail Electric Providers (REPs) and LSEs.  QSEs and TOs shall establish and maintain internal procedures for contingency preparedness or to expedite the resolution of the conditions communicated by ERCOT that threaten system reliability.

(4)	Before deciding which emergency communication to issue, ERCOT must consider the possible severity of the operating situation before an Emergency Condition occurs.  If practicable, the market shall be allowed to attempt to mitigate or eliminate any possible Emergency Condition.  ERCOT has the responsibility to issue the appropriate communications to facilitate a solution by Market Participants.

4.2	Communication Under Emergency Conditions

4.2.1	Operating Condition Notice

(1)	An Operating Condition Notice (OCN) shall be issued by ERCOT in accordance with Protocol Section 6.5.9.3.1, Operating Condition Notice.  OCNs are for communication purposes only.

(2)	ERCOT may require information from Qualified Scheduling Entities (QSEs) and Transmission Operators (TOs).  Typical information requested may include, but is not limited to:

(a)	Resource fuel capabilities;

(b)	Resource condition details; and

(c)	Actual weather conditions.

(3)	ERCOT will provide verbal notice of an OCN to all TOs and QSEs representing Resources and post the message electronically to the Market Information System (MIS) Public Area.  When an OCN is issued, it does not place ERCOT in an Emergency Condition.  QSEs should notify appropriate Resources, Retail Electric Providers (REPs) and Load Serving Entities (LSEs).  TOs should notify their represented Transmission Service Providers (TSPs) as appropriate.

[NOGRR177: Replace paragraph (3) above with the following upon system implementation of NPRR857:] (3) ERCOT will provide verbal notice of an OCN to all TOs and QSEs representing Resources and post the message electronically to the Market Information System (MIS) Public Area. When an OCN is issued, it does not place ERCOT in an Emergency Condition. QSEs should notify appropriate Resources, Retail Electric Providers (REPs) and Load Serving Entities (LSEs). TOs should notify their represented Transmission Service Providers (TSPs) and Direct Current Tie Operators (DCTOs) as appropriate.

4.2.2	Advisory

(1)	An Advisory will be issued by ERCOT in accordance with Protocol Section 6.5.9.3.2, Advisory, when it recognizes that conditions are developing or have changed such that QSE and/or TO actions may be prudent in response to impending Emergency Conditions.

(2)	ERCOT may require information from QSEs and TOs.  Typical information requested may include, but is not limited to:

(a)	Resource fuel capabilities;

(b)	Resource condition details; and

(c)	Actual weather conditions.

(3)	When an Advisory is issued for Physical Responsive Capability (PRC) below 3,000 MW and ERCOT expects system conditions to deteriorate to the extent that an Energy Emergency Alert (EEA) Level 2 or 3 may be experienced, ERCOT shall evaluate constraints active in Security-Constrained Economic Dispatch (SCED) and determine which constraints have the potential to limit generation output.

(a)	Upon identification of such constraints, ERCOT shall coordinate with the TSPs that own or operate the overloaded Transmission Facilities associated with those constraints, as well as the Resource Entities whose generation output may be limited, to determine whether:

[NOGRR177: Replace paragraph (a) above with the following upon system implementation of NPRR857:] (a) Upon identification of such constraints, ERCOT shall coordinate with the TSPs and DCTOs that own or operate the overloaded Transmission Facilities associated with those constraints, as well as the Resource Entities whose generation output may be limited, to determine whether:

(i) 	A 15-Minute Rating is available that allows for additional transmission capacity for use in congestion management, if an EEA Level 2 or 3 is declared, and post-contingency actions can be taken within 15 minutes to return the flow to within the Emergency Rating.  Such actions may include, but are not limited to, reducing the generation that increased output as a result of enforcing the 15-Minute Rating rather than the Emergency Rating;

(ii)	Post-contingency loading of the Transmission Facilities is expected to be at or below Normal Rating within two hours; or

(iii)	Additional transmission capacity could allow for additional output from a limited Generation Resource by taking one of the following actions:

- Restoring Transmission Elements that are out of service:

- Reconfiguring the transmission system; or

- Making adjustments to phase angle regulator tap positions.

If ERCOT determines that one of the above-mentioned actions allows for additional output from a limited Generation Resource, ERCOT may instruct the TSPs to take the action(s) during the Advisory to allow for additional output from the limited Generation Resource.

(b) 	ERCOT shall also coordinate with TSPs who own and operate the Transmission Facilities associated with the double-circuit contingencies for the constraints identified above to determine whether the double-circuit failures are at a high risk of occurring due to system conditions, which may include: severe weather conditions forecasted by ERCOT in the vicinity of the double-circuit, weather conditions that indicate a high risk of insulator flashover on the double-circuit, repeated Forced Outages of the individual circuits that are part of the double-circuit in the preceding 48 hours, or fire in progress in the right of way of the double-circuit.

[NOGRR177: Replace paragraph (b) above with the following upon system implementation of NPRR857:] (b) ERCOT shall also coordinate with TSPs and DCTOs who own and operate the Transmission Facilities associated with the double-circuit contingencies for the constraints identified above to determine whether the double-circuit failures are at a high risk of occurring due to system conditions, which may include: severe weather conditions forecasted by ERCOT in the vicinity of the double-circuit, weather conditions that indicate a high risk of insulator flashover on the double-circuit, repeated Forced Outages of the individual circuits that are part of the double-circuit in the preceding 48 hours, or fire in progress in the right of way of the double-circuit.

(c)	The actions detailed in this Section shall be supplemental to the development and maintenance of Constraint Management Plans (CMPs) as otherwise directed by the Protocols or Operating Guides.

(4)	ERCOT shall provide verbal notice of an Advisory to all TOs and QSEs representing Resources and shall post the message electronically to the MIS Public Area.  When an Advisory is issued, it does not place ERCOT in an Emergency Condition.  QSEs shall notify appropriate Resources, REPs and LSEs of Advisories.  TOs should notify their represented TSPs as appropriate of Advisories.

[NOGRR177: Replace paragraph (4) above with the following upon system implementation of NPRR857:] (4) ERCOT shall provide verbal notice of an Advisory to all TOs and QSEs representing Resources and shall post the message electronically to the MIS Public Area. When an Advisory is issued, it does not place ERCOT in an Emergency Condition. QSEs shall notify appropriate Resources, REPs, and LSEs of Advisories. TOs should notify their represented TSPs or DCTOs as appropriate of Advisories.

4.2.3	Watch

(1)	A Watch may be issued by ERCOT in accordance with Protocol Section 6.5.9.3.3, Watch, when it recognizes that conditions have developed such that an Emergency Condition exists or is imminent.

(2)	ERCOT may require information from QSEs and TOs.  Typical information requested may include, but is not limited to:

(a)	Resource fuel capabilities;

(b)	Resource condition details; and

(c)	Actual weather conditions.

(3)	When a post-contingency overload of an element cannot be rectified, including through the use of CMPs, ERCOT shall issue a Watch.

(4)	ERCOT shall provide verbal notice of the Watch to all TOs and QSEs representing Resources and shall post the message electronically to the MIS Public Area.  QSEs shall notify appropriate Resources, REPs and LSEs.  TOs shall notify their represented TSPs.

[NOGRR177: Replace paragraph (4) above with the following upon system implementation of NPRR857:] (4) ERCOT shall provide verbal notice of the Watch to all TOs and QSEs representing Resources and shall post the message electronically to the MIS Public Area. QSEs shall notify appropriate Resources, REPs, and LSEs. TOs shall notify their represented TSPs or DCTOs.

4.2.4	Emergency Notice

(1)	An Emergency Notice will be issued by ERCOT in accordance with Protocol Section 6.5.9.3.4, Emergency Notice, when ERCOT is operating in an Emergency Condition.  This includes when ERCOT is considered to be in an insecure state when ERCOT Transmission Grid status is such that a Credible Single Contingency event presents the threat of uncontrolled separation of cascading Outages and/or large-scale service disruption to Load (other than Load being served from a single-feed transmission service) and/or overload of a Transmission Facility, and no timely solution is obtainable from the market.

(2)	ERCOT shall provide verbal notice of an Emergency Notice to all TOs and QSEs representing Resources and shall post the message electronically to the MIS Public Area.

(3)	When an Emergency Notice is issued, ERCOT is operating in an Emergency Condition.  QSEs shall notify appropriate Resources, REPs and LSEs.  TOs shall notify their represented TSPs and LSEs.

[NOGRR177: Replace paragraph (3) above with the following upon system implementation of NPRR857:] (3) When an Emergency Notice is issued, ERCOT is operating in an Emergency Condition. QSEs shall notify appropriate Resources, REPs and LSEs. TOs shall notify their represented TSPs, DCTOs, and LSEs.

4.3	Operation to Maintain Transmission System Security

(1)	ERCOT shall continue to operate according to Security Criteria outlined in Section 2.2.2, Security Criteria, unless an Emergency Condition has been declared by ERCOT.

(2)	Transmission Overload – ERCOT can:

(a)	Order adjustment to unit generation schedules, switching of Transmission Elements or Load interruption to relieve the overloaded Transmission Element;

(b)	Order a Transmission Element whose loss would not have a significant impact on the reliability of transmission system switched out to increase interconnected system transfers.

(3)	Violation of security criteria – ERCOT can order changes to unit dispatch or commitment to eliminate or avoid a security criteria violation.  Normally these changes should be performed through market control mechanisms including Security-Constrained Economic Dispatch (SCED) or Reliability Unit Commitment (RUC) as described in the Protocols, but if an ERCOT Operator finds these mechanisms insufficient to resolve the violation, the ERCOT Operator may require any other action necessary to address the violation.

(4)	Partial Blackout or Blackout – ERCOT shall implement Black Start procedures.

4.3.1	Real-Time and Short Term Planning

(1)	ERCOT will conduct Real-Time and short term planning based on the security criteria established in these Operating Guides.  Operations during Forced and Planned Outages will also follow these criteria.  Line Ratings are provided to ERCOT in accordance with Protocols and these Operating Guides.  ERCOT will employ Constraint Management Plans (CMPs) and use of Remedial Action Schemes (RASs) to facilitate the use of the ERCOT Transmission Grid while maintaining system security and reliability in accordance with the Protocols, these Operating Guides, and applicable North American Electric Reliability Corporation (NERC) Reliability Standards.  ERCOT will address operating conditions under which the reliability of the ERCOT System is inadequate and no solution is readily apparent in accordance with the Protocols and these Operating Guides.

4.4	Block Load Transfers between ERCOT and Non-ERCOT System

(1)	Under Watch, Energy Emergency Alert (EEA) conditions, or for local transmission constraints, it may become necessary to implement Block Load Transfer (BLT) schemes which will transfer Loads normally located in ERCOT to a non-ERCOT System.  Similarly, when a non-ERCOT System experiences certain transmission contingency or short supply conditions, ERCOT may be requested to transfer Loads normally located in the non-ERCOT System to ERCOT.  All BLTs must comply with Protocol Section 6.5.9.5, Block Load Transfers between ERCOT and Non-ERCOT Control Areas.

4.5	Energy Emergency Alert (EEA)

4.5.1	General

(1)	At times it may be necessary to reduce ERCOT System demand because of a temporary decrease in available electricity supply.  The reduction in supply could be caused by emergency Outages of generators, transmission equipment, or other critical facilities; by short-term unavailability of fuel or generation; or by requirements or orders of government agencies.  To provide an orderly, predetermined procedures for curtailing Demand during such emergencies, ERCOT shall initiate and coordinate the implementation of the Energy Emergency Alert (EEA) in accordance with Protocol Section 6.5.9.4, Energy Emergency Alert.

(2)	The goal of the EEA is to provide for maximum possible continuity of service while maintaining the integrity of the ERCOT System to reduce the chance of cascading outages.

4.5.2	Operating Procedures

(1)	The ERCOT System Operators have the authority to make and carry through decisions that are required to operate the ERCOT System during emergency or adverse conditions.  ERCOT will have sufficiently detailed operating procedures for emergency or short supply situations and for restoration of service in the event of a Partial Blackout or Blackout.  These procedures will be distributed to the personnel responsible for performing specified tasks to handle emergencies, remedy short supply situations, or restore service.  Transmission Service Providers (TSPs) will develop procedures to be filed with ERCOT describing implementation of ERCOT requests in emergency and short supply situations, including interrupting Load, notifying others and restoration of service.

[NOGRR177: Replace paragraph (1) above with the following upon system implementation of NPRR857:] (1) The ERCOT System Operators have the authority to make and carry through decisions that are required to operate the ERCOT System during emergency or adverse conditions. ERCOT will have sufficiently detailed operating procedures for emergency or short supply situations and for restoration of service in the event of a Partial Blackout or Blackout. These procedures will be distributed to the personnel responsible for performing specified tasks to handle emergencies, remedy short supply situations, or restore service. Transmission Service Providers (TSPs) and Direct Current Tie Operators (DCTOs) will develop procedures to be filed with ERCOT describing implementation of ERCOT requests in emergency and short supply situations, including interrupting Load, notifying others and restoration of service.

(2)	ERCOT and each TSP will endeavor to maintain transmission ties intact if at all possible.  This will:

(a) 	Permit rendering the maximum assistance to an area experiencing a deficiency in generation;

(b) 	Minimize the possibility of cascading loss to other parts of the system; and

(c) 	Assist in restoring operation to normal.

[NOGRR177: Replace paragraph (2) above with the following upon system implementation of NPRR857:] (2) ERCOT and Transmission Operators (TOs) will endeavor to maintain transmission ties intact if at all possible. This will: (a) Permit rendering the maximum assistance to an area experiencing a deficiency in generation; (b) Minimize the possibility of cascading loss to other parts of the system; and (c) Assist in restoring operation to normal.

(3)	ERCOT's operating procedures will meet the following goals while continuing to respect the confidentiality of market sensitive data.  If all goals cannot be respected simultaneously then the priority order listed below shall be respected:

(a)	Maintain station service for nuclear generating facilities;

(b)	Securing startup power for power generating plants;

(c)	Operating generating plants isolated from ERCOT without communication;

(d)	Restoration of service to critical Loads such as:

(i)	Military facilities;

(ii)	Facilities necessary to restore the electric utility system;

(iii)	Law enforcement organizations and facilities affecting public health; and

(iv)	Communication facilities.

(e)	Maximum utilization of ERCOT System capability;

(f)	Utilization of Responsive Reserve (RRS) services and other Ancillary Services to the extent permitted by ERCOT System conditions;

[NOGRR187: Replace paragraph (f) above with the following upon system implementation of NPRR863:] (f) Utilization of Ancillary Services to the extent permitted by ERCOT System conditions;

(g)	Utilization of the market to the fullest extent practicable without jeopardizing the reliability of the ERCOT System;

(h)	Restoration of service to all Customers following major system disturbances, giving priority to the larger group of Customers; and

(i) 		Management of Interconnection Reliability Operating Limits (IROLs) shall not change.

4.5.3	Implementation

(1)	ERCOT shall be responsible for monitoring system conditions, initiating the EEA levels below, notifying all Qualified Scheduling Entities (QSEs) and TOs, and coordinating the implementation of the EEA conditions while maintaining transmission security limits.  QSEs and TOs will notify all the Market Participants they represent of each declared EEA level.

(2)	During the EEA, ERCOT has the authority to obtain energy from non-ERCOT Control Areas using Direct Current Tie(s) (DC Tie(s)) or by using Block Load Transfers (BLTs) to move load to non-ERCOT Control Areas.  ERCOT maintains the authority to curtail energy schedules flowing into or out of the ERCOT System across the DC Ties in accordance with North American Electric Reliability Corporation (NERC) scheduling guidelines.

(3) 	ERCOT, at management’s discretion, may at any time issue an ERCOT-wide appeal through the public news media for voluntary energy conservation.

(4)	There may be insufficient time to implement all levels in sequence.  ERCOT may immediately implement Level 3 of the EEA any time the clock-minute average system frequency falls below 59.91 Hz for 20 consecutive minutes and shall immediately implement Level 3 any time the steady-state frequency is below 59.5 Hz for any duration.

(5)	Percentages for Level 3 Load shedding will be based on the previous year’s TSP peak Loads, as reported to ERCOT, and will be reviewed by ERCOT and modified annually.

(6)	The ERCOT System Operator shall declare the EEA levels to be taken by QSEs and TSPs.  QSEs and TSPs shall implement actions under that level (and all above if not previously accomplished) and if ordered by the ERCOT shift supervisor or his designate, shall report back to the ERCOT System Operator when the requested level has been completed.

[NOGRR177: Replace paragraph (6) above with the following upon system implementation of NPRR857:] (6) The ERCOT System Operator shall declare the EEA levels to be taken by QSEs, TSPs, and DCTOs. QSEs, TSPs, and DCTOs shall implement actions under that level (and all above if not previously accomplished) and if ordered by the ERCOT shift supervisor or his designate, shall report back to the ERCOT System Operator when the requested level has been completed.

(7)	During EEA Level 3, ERCOT must be capable of shedding sufficient firm Load to arrest frequency decay and to prevent generator tripping.  The amount of firm Load to be shed may vary depending on ERCOT Transmission Grid conditions during the event.  Each TSP will be capable of shedding its allocation of firm Load, without delay.  The maximum time for the TSP to interrupt firm Load will depend on how much Load is to be shed and whether the Load is to be interrupted by Supervisory Control and Data Acquisition (SCADA) or by the dispatch of personnel to substations.  Since the need for firm Load shed is immediate, interruption by SCADA is preferred.  The following requirements apply for an ERCOT instruction to shed firm Load:

(a)	Load interrupted by SCADA will be shed without delay and in a time period not to exceed 30 minutes;

(b)	Load interrupted by dispatch of personnel to substations to manually shed Load will be implemented within a time period not to exceed one hour;

(c)	The initial clock on the firm Load shed shall apply only to Load shed amounts up to 1000 MW total.  Load shed amount requests exceeding 1000 MW on the initial clock may take longer to implement; and

(d)	If, after the first Load shed instruction, ERCOT determines that an additional amount of firm Load should be shed, another clock will begin anew.  The time frames mentioned above will apply.

(8)	Each TSP, or its designated agent, will provide ERCOT a status report of Load shed progress within 30 minutes of the time of ERCOT’s instruction or upon ERCOT’s request.

(9)	During EEA Level 2 or 3, for those constraints that meet the criteria identified in paragraph (3)(a) of Section 4.2.2, Advisory, ERCOT may control the post-contingency flow to within the 15-Minute Rating in SCED.   After Physical Responsive Capability (PRC) is restored to at least 3,000 MW or the Emergency Condition has ended, whichever is later, and ERCOT has determined that system conditions have improved such that the chance of re-entering into an EEA Level 2 or 3 is low, ERCOT shall restore control to the post-contingency flow to within the Emergency Rating for these constraints that utilized the 15-Minute Rating in Security Constrained Economic Dispatch (SCED).

(10)	During EEA Level 2 or 3, for those constraints that meet the criteria identified in paragraph (3)(b) of Section 4.2.2, ERCOT shall continue to enforce constraints associated with double-circuit contingencies throughout an EEA if the double-circuit failures are determined to be at high risk of occurring, due to system conditions.  For all other double-circuit contingencies identified in paragraph (3)(b) of Section 4.2.2, ERCOT will enforce only the associated single-circuit contingencies during EEA Level 2 or 3.  ERCOT shall resume enforcing such constraints as a double-circuit contingency after PRC is restored to at least 3,000 MW or the Emergency Condition has ended, whichever is later, and ERCOT has determined that system conditions have improved such that the chance of re-entering into an EEA Level 2 or 3 is low.  For constraints related to stability limits that are not IROLs, ERCOT may elect not to enforce double-circuit contingencies during EEA Level 3 only.

4.5.3.1 	General Procedures Prior to EEA Operations

(1)	Prior to declaring EEA Level 1 detailed in Section 4.5.3.3, EEA Levels, ERCOT may perform the following operations consistent with Good Utility Practice:

(a)	Provide Dispatch Instructions to QSEs for specific Resources to operate at an Emergency Base Point to maximize Resource deployment so as to increase Responsive Reserve levels on other Resources;

(b)	Commit specific available Resources as necessary that can respond in the timeframe of the emergency.  Such commitments will be settled using the Hourly Reliability Unit Commitment (HRUC) process;

(c)	Start Reliability Must-Run (RMR) Units available in the time frame of the emergency.  RMR Units should be loaded to full capability;

(d)	Utilize available Resources providing Non-Spinning Reserve (Non-Spin) services as required; and

(e)	ERCOT shall use the PRC and system frequency to determine the appropriate Emergency Notice and EEA levels.

4.5.3.2	General Procedures During EEA Operations

(1)		ERCOT Control Area authority will re-emphasize the following operational practices during EEA operations to minimize non-performance issues that may result from the pressures of the emergency situation.

(a)	ERCOT shall suspend Ancillary Service obligations that it deems to be contrary to reliability needs;

(b)	ERCOT shall notify each QSE and TO via Hotline of declared EEA level;

(c)	QSEs and TOs shall notify each represented Market Participant of declared EEA level;

(d)	ERCOT, QSEs and TSPs shall continue to respect confidential market sensitive data;

[NOGRR177: Replace paragraph (d) above with the following upon system implementation of NPRR857:] (d) ERCOT, QSEs, TSPs, and DCTOs shall continue to respect confidential market sensitive data;

(e)	QSEs shall update Current Operating Plans (COPs) to limit or remove capacity when unexpected start-up delays occur or when ramp limitations are encountered;

(f)	QSEs shall report when On-Line or available capacity is at risk due to adverse circumstances;

(g)	QSEs, TSPs, and all other Entities must not suspend efforts toward expeditious compliance with the applicable EEA level declared by ERCOT nor initiate any reversals of required actions without ERCOT authorization;

[NOGRR177: Replace paragraph (g) above with the following upon system implementation of NPRR857:] (g) QSEs, TSPs, DCTOs, and all other Entities must not suspend efforts toward expeditious compliance with the applicable EEA level declared by ERCOT nor initiate any reversals of required actions without ERCOT authorization;

(h)	ERCOT shall define procedures for determining the proper redistribution of reserves during EEA operations; and

(i) 	QSEs shall not remove an On-Line Generation Resource without prior ERCOT authorization unless such actions would violate safety, equipment, or regulatory or statutory requirements.  Under these circumstances, QSEs shall immediately inform ERCOT of the need and reason for removing the On-Line Generation Resource from service.

4.5.3.3	EEA Levels

(1)	ERCOT will declare an EEA Level 1 when PRC falls below 2,300 MW and is not projected to be recovered above 2,300 MW within 30 minutes without the use of the following actions that are prescribed for EEA Level 1:

(a)	ERCOT shall take the following steps to maintain steady state system frequency near 60 Hz and maintain PRC above 1,750 MW:

(i)	Request available Generation Resources, that can perform within the expected timeframe of the emergency, to come On-Line by initiating manual HRUC or through Dispatch Instructions;

(ii)	Use available DC Tie import capacity that is not already being used;

(iii)	Issue a Dispatch Instruction for Resources to remain On-Line which, before start of emergency, were scheduled to come Off-Line; and

(iv)	At ERCOT’s discretion, deploy available contracted Emergency Response Service (ERS)-30 via an Extensible Markup Language (XML) message followed by a Verbal Dispatch Instruction (VDI) to the all-QSE Hotline.  The ERS-30 ramp period shall begin at the completion of the VDI.

(A)	If less than 500 MW of ERS-30 is available for deployment, ERCOT shall deploy it as a single block.

(B)	If the amount of ERS-30 available for deployment equals or exceeds 500 MW, ERCOT, at its discretion, may deploy ERS-30 as a single block or by group designation.  ERCOT shall develop a random selection methodology for determining how to place ERS Resources in ERS-30 into groups, and shall describe the methodology in a document posted to the Market Information System (MIS) Public Area.  Prior to the start of an ERS Contract Period for ERS-30, ERCOT shall notify QSEs representing ERS Resources in ERS-30 of their ERS Resources’ group assignments.

(C)	ERS-30 may be deployed at any time in a Settlement Interval.

(D)	Upon deployment, QSEs shall instruct their ERS Resources in ERS-30 to perform at contracted levels consistent with the criteria described in Section 8.1.3.1.4, Event Performance Criteria for Emergency Response Service Resources, until either ERCOT releases the ERS-30 deployment or the ERS-30 Resources have reached their maximum deployment time.

(E)	ERCOT shall notify QSEs of the release of ERS-30 via an XML message followed by VDI to the all-QSE Hotline.  The VDI shall represent the official notice of ERS-30 release.  ERCOT may release ERS-30 as a block or by group designation.

(F)	Upon release, an ERS Resource in ERS-30 shall return to a condition such that it is capable of meeting its ERS performance requirements as soon as practical, but no later than ten hours following the release.

(b)	QSEs shall:

(i)	Ensure COPs and telemetered High Sustained Limits (HSLs) are updated and reflect all Resource delays and limitations; and

(ii)	Suspend any ongoing ERCOT-required Resource performing testing.

(2)	ERCOT may declare an EEA Level 2 when the clock-minute average system frequency falls below 59.91 Hz for 15 consecutive minutes.  ERCOT will declare an EEA Level 2 when PRC falls below 1,750 MW and is not projected to be recovered above 1,750 MW within 30 minutes without the use of the following actions that are prescribed for EEA Level 2:

(a)	In addition to the measures associated with EEA Level 1, ERCOT shall take the following steps to maintain steady state system frequency at a minimum of 59.91 Hz and maintain PRC above 1,375 MW:

(i)	Instruct TSPs and Distribution Service Providers (DSPs) or their agents to reduce Customer Load by using distribution voltage reduction measures, if deemed beneficial by the TSP, DSP or their agents;

(ii)	Instruct TSPs and DSPs to implement any available Load management plans to reduce Customer Load;

(iii)	Instruct QSEs to deploy available contracted ERS-10 Resources, undeployed ERS-30 and/or deploy RRS supplied from Load Resources (controlled by high-set under-frequency relays).  ERCOT may deploy ERS-10, ERS-30 or RRS simultaneously or separately, and in any order.  ERCOT shall issue such Dispatch Instructions in accordance with the deployment methodologies described in paragraphs (iv) and (v) below and, if deploying ERS-30, the methodologies described in paragraph (1)(a)(iv) above.

[NOGRR186: Replace paragraph (iii) above with the following upon system implementation of NPRR863:] (iii) Instruct QSEs to deploy available contracted ERS-10 Resources, undeployed ERS-30, and/or deploy ERCOT Contingency Reserve Service (ECRS) or RRS (controlled by high-set under-frequency relays) supplied from Load Resources. ERCOT may deploy ERS-10, ERS-30, ECRS, or RRS simultaneously or separately, and in any order. ERCOT shall issue such Dispatch Instructions in accordance with the deployment methodologies described in paragraphs (iv) and (v) below and, if deploying ERS-30, the methodologies described in paragraph (1)(a)(iv) above.

(iv)	ERCOT shall deploy ERS-10 via an XML message followed by a VDI to the all-QSE Hotline.  The ERS-10 ramp period shall begin at the completion of the VDI.

(A)	If less than 500 MW of ERS-10 is available for deployment, ERCOT shall deploy all ERS-10 Resources as a single block.

(B)	If the amount of ERS-10 available for deployment equals or exceeds 500 MW, ERCOT, at its discretion, may deploy ERS-10 Resources as a single block or by group designation.  ERCOT shall develop a random selection methodology for determining how to place ERS-10 Resources into groups, and shall describe the methodology in a document posted to the MIS Public Area.  Prior to the start of an ERS-10 Contract Period, ERCOT shall notify QSEs representing ERS-10 Resources of their ERS-10 Resources’ group assignments.

(C)	ERS-10 may be deployed at any time in a Settlement Interval.

(D)	Upon deployment, QSEs shall instruct ERS-10 Resources to perform at contracted levels consistent with the criteria described in Protocol Section 8.1.3.1.4 until ERCOT releases the ERS-10 deployment or the ERS-10 Resources have reached their maximum deployment times.

(E)	ERCOT shall notify QSEs of the release of ERS-10 via an XML message followed by VDI to the all-QSE Hotline.  The VDI shall represent the official notice of ERS-10 release. ERCOT may release ERS-10 as a block or by group designation.

(F)	Upon release, an ERS-10 Resource shall return to a condition such that it is capable of meeting its ERS performance requirements as soon as practical, but no later than ten hours following the release.

(v)	ERCOT shall deploy RRS capacity supplied by Load Resources (controlled by high-set under-frequency relays) in accordance with the following:

[NOGRR186: Replace paragraph (v) above with the following upon system implementation of NPRR863:] (v) Load Resources providing ECRS that are not controlled by high set under-frequency relays shall be deployed prior to Group 1 deployment. ERCOT shall deploy ECRS and RRS capacity supplied by Load Resources (controlled by high-set under-frequency relays) in accordance with the following:

(A)	Instruct QSEs to deploy half of the RRS that is supplied from Load Resources (controlled by high-set under-frequency relays) by instructing the QSE representing the specific Load Resource to interrupt Group 1 Load Resources providing RRS.  QSEs shall deploy Load Resources according to the group designation and will be given some discretion to deploy additional Load Resources from Group 2 if Load Resource operational considerations require such.  ERCOT shall issue notification of the deployment via XML message.  ERCOT shall follow this XML notification with a Hotline VDI, which shall initiate the ten-minute deployment period;

[NOGRR186 and NOGRR198: Replace applicable portions of paragraph (A) above with the following upon system implementation of NPRR863 or NPRR939:] (A) Instruct QSEs to deploy RRS with a Group 1 designation and all of the ECRS that is supplied from Load Resources (controlled by high-set under-frequency relays) by instructing the QSE representing the specific Load Resources to interrupt Group 1 Load Resources providing ECRS and RRS. QSEs shall deploy Load Resources according to the group designation and will be given some discretion to deploy additional Load Resources from any of the groups not designated for deployment if Load Resource operational considerations require such. ERCOT shall issue notification of the deployment via XML message. ERCOT shall follow this XML notification with a Hotline VDI, which shall initiate the ten-minute deployment period;

(B)	At the discretion of the ERCOT Operator, instruct QSEs to deploy the remaining RRS that is supplied from Load Resources (controlled by high-set under-frequency relays) by instructing the QSE representing the specific Load Resource to interrupt Group 2 Load Resources providing RRS.  ERCOT shall issue notification of the deployment via XML message.  ERCOT shall follow this XML notification with a Hotline VDI, which shall initiate the ten-minute deployment period;

[NOGRR198: Replace paragraph (B) above with the following upon system implementation of NPRR939:] (B) At the discretion of the ERCOT Operator, instruct QSEs to deploy RRS that is supplied from Load Resources (controlled by high-set under-frequency relays) by instructing the QSE representing the specific Load Resource to interrupt additional Load Resources providing RRS based on their group designation. ERCOT shall issue notification of the deployment via XML message. ERCOT shall follow this XML notification with a Hotline VDI, which shall initiate the ten-minute deployment period;

(C)	The ERCOT Operator may deploy both of the groups of Load Resources providing RRS at the same time.  ERCOT shall issue notification of the deployment via XML message.  ERCOT shall follow this XML notification with a Hotline VDI, which shall initiate the ten-minute deployment period; and

[NOGRR186 and NOGRR198: Replace applicable portions of paragraph (C) above with the following upon system implementation of NPRR863 or NPRR939:] (C) The ERCOT Operator may deploy Load Resources providing only ECRS (not controlled by high-set under-frequency relays) and all groups of Load Resources providing RRS and ECRS at the same time. ERCOT shall issue notification of the deployment via XML message. ERCOT shall follow this XML notification with a Hotline VDI, which shall initiate the ten-minute deployment period; and

(D)	ERCOT shall post a list of Load Resources on the MIS Certified Area immediately following the Day-Ahead Reliability Unit Commitment (DRUC) for each QSE with a Load Resource obligation which may be deployed to interrupt under paragraph (A), Group 1 and paragraph (B), Group 2.  ERCOT shall develop a process for determining which individual Load Resource to place in Group 1 and which to place in Group 2.  ERCOT procedures shall select Group 1 and Group 2 based on a random sampling of individual Load Resources.  At ERCOT’s discretion, ERCOT may deploy all Load Resources at any given time during EEA Level 2.

[NOGRR198: Replace paragraph (D) above with the following upon system implementation of NPRR939:] (D) ERCOT shall post a list of Load Resources on the MIS Certified Area immediately following the DRUC for each QSE with a Load Resource obligation which may be deployed to interrupt under paragraph (A) and paragraph (B). ERCOT shall develop a process for determining which individual Load Resource to place in each group based on a random sampling of individual Load Resources. At ERCOT’s discretion, ERCOT may deploy all Load Resources at any given time during EEA Level 2.

(vi)	Unless a media appeal is already in effect, ERCOT shall issue an appeal through the public news media for voluntary energy conservation; and

(vii)	With the approval of the affected non-ERCOT Control Area, TSPs, DSPs, or their agents may implement BLTs, which transfer Load from the ERCOT Control Area to non-ERCOT Control Areas in accordance with BLTs as defined in the Operating Guides.

(b)	Confidentiality requirements regarding transmission operations and system capacity information will be lifted, as needed to restore reliability.

(3)	ERCOT may declare an EEA Level 3 when the clock-minute average system frequency falls below 59.91 Hz for 20 consecutive minutes.  ERCOT will declare an EEA Level 3 when PRC cannot be maintained above 1,375 MW or when the clock-minute average system frequency falls below 59.91 Hz for 25 consecutive minutes.  Upon declaration of an EEA Level 3, ERCOT will implement any measures associated with EEA Levels 1 and 2 that have not already been implemented.

(a)	When PRC falls below 1,000 MW and is not projected to be recovered above 1,000 MW within 30 minutes, or when the clock-minute average frequency falls below 59.91 Hz for 25 consecutive minutes, ERCOT shall direct all TSPs and DSPs or their agents to shed firm Load, in 100 MW blocks, distributed as documented in these Operating Guides in order to maintain a steady state system frequency at a minimum of 59.91 Hz and to recover 1,000 MW of PRC within 30 minutes.

(b)	In addition to measures associated with EEA Levels 1 and 2, TSPs and DSPs or their agents will keep in mind the need to protect the safety and health of the community and the essential human needs of the citizens.  Whenever possible, TSPs and DSPs or their agents shall not manually drop Load connected to under-frequency relays during the implementation of the EEA.

- 4.5.3.4	Load Shed Obligation

(1)	Obligation for Load shed is by DSP.  Load shedding obligations need to be represented by an Entity with 24x7 operations and Hotline communications with ERCOT and control over breakers.  Percentages for Level 3 Load shedding will be based on the previous year’s TSP peak Loads, as reported to ERCOT, and will be reviewed by ERCOT and modified annually.  (Use TOs as list of Entities)

ERCOT Load Shed Table

| Transmission Operator | 2018 Total Transmission Operator Load (%MW) |
| --- | --- |
| AEP Texas Central Company | 8.52 |
| Brazos Electric Power Cooperative Inc. | 5.24 |
| Brownsville Public Utilities Board | 0.36 |
| Bryan Texas Utilities | 0.49 |
| CenterPoint Energy Houston Electric LLC | 24.27 |
| City of Austin DBA Austin Energy | 3.6 |
| City of Brady | 0.02 |
| City of College Station | 0.28 |
| City of Garland | 0.9 |
| CPS Energy (San Antonio) | 6.53 |
| Denton Municipal Electric | 0.50 |
| GEUS (Greenville) | 0.16 |
| LCRA Transmission Services Corporation | 5.74 |
| Oncor Electric Delivery Company LLC | 37.43 |
| Rayburn Country Electric Cooperative Inc. DBA Rayburn Electric | 1.19 |
| South Texas Electric Cooperative Inc. | 2.21 |
| Texas-New Mexico Power Company | 2.56 |
| ERCOT Total | 100.00 |

- 4.5.3.5	EEA Termination

(1)	ERCOT shall:

(a)	Continue EEA until sufficient Resources are available to ERCOT to eliminate the shortfall and restore adequate reserves;

(b)	Restore full reserve requirements (normally 2300 MW);

(c)	Terminate the levels in reverse order, where practical;

(d)	Notify each QSE and TO of EEA level termination; and

(e)	Maintain a stable ERCOT System frequency when restoring Load.

(2)	QSEs and TOs shall:

(a)	Implement actions to terminate previous actions as EEA levels are released in accordance with these Operating Guides;

(b)	Notify represented Market Participants of EEA levels changes;

(c)	Report back to the ERCOT System Operator when each level is accomplished; and

(d)	Loads will be restored when specifically authorized by the ERCOT.

4.6	Black Start Service

(1)	This section provides general guidelines to be followed in the event of a Partial Blackout or Blackout of the ERCOT System.  Timely implementation of a Black Start plan compiled in accordance with Section 8, Attachment E, Black Start Plan Template, should facilitate coordination between ERCOT, Qualified Scheduling Entities (QSEs) who represent Black Start Resources, Black Start Resources, and Transmission Operators (TOs) and ensure restoration of service to the ERCOT System at the earliest possible time.  The Authorized Representative for Resource Entities that own contracted Black Start Resources will provide their QSE and ERCOT with a copy of the individual plant start-up procedures for coordination of their activities with those of the appropriate TO.

(2)	Pre-established plans and procedures cannot foresee all the possible combinations of system problems that may occur after a major failure.  It is the responsibility of ERCOT to restore the system to normal, applying the principles, strategies, and priorities outlined in the ERCOT Black Start Plan.

4.6.1	Principles

(1)	In order to minimize the time required, ERCOT will develop the Black Start Plan to utilize the principles, strategies, and priorities outlined in this Guide.  The ERCOT Black Start Plan shall be coordinated with local TO Black Start plans to provide a coordinated Black Start reference.

(2)	Each contracted Black Start Resource and each QSE with contracted Black Start Resource(s) will have readily accessible and sufficiently detailed current operating procedures to assist in an orderly recovery.

(3)	Mutual assistance and cooperation will be essential during the restoration.  Deliberate, careful action by each QSE, TO, and Resource Entity is necessary to minimize the length of time required for restoration and to avoid the reoccurrence of a Partial Blackout or Blackout of the ERCOT System.

(4)	Throughout the restoration, recovery will depend on ERCOT receiving an accurate assessment of system conditions and status from each QSE, TO, and Resource Entity throughout the restoration.  Adequate and reliable communications must be available within the ERCOT System.  During Black Start recovery, communication restrictions may enable the sharing of market sensitive information that pertains to the restoration of the ERCOT System.  This includes but is not limited to availability status and recovery activities.

4.6.2	Strategies

(1)	In the event of a Partial Blackout or Blackout of the ERCOT System, immediate steps must be taken to return the interconnected network to normal as quickly as possible.  For detailed Black Start information, refer to Section 8, Attachment A, Detailed Black Start Information.

(a)	Each TO shall immediately initiate its portion of the ERCOT Black Start Plan and attempt to establish contact with ERCOT.  If communications with ERCOT are unavailable the TO shall immediately establish communications with its interconnected Black Start Resource(s) and the Black Start Resource’s QSE.

(b)	Each QSE representing Black Start Resources shall initiate communications with its Black Start Resources and immediately notify ERCOT and the appropriate TO of their condition and status.

(c)	Available Black Start Resources shall immediately start their isolation and startup procedures and attempt to establish communications with the local TO.

(d)	As generating and transmission capabilities become available, systematic restoration of ERCOT Load with respect to priorities shall begin in accordance with the local TO Black Start plans, taking care to balance Load and generating capability while maintaining an acceptable frequency.

(e)	Appropriate voltage levels and reactive control must be maintained during the restoration.  Consideration should be given to connecting Islands at locations having communications, frequency control, voltage control, synchronization facilities, and adequate transmission capacity.  ERCOT will coordinate the return to full Automatic Generation Control (AGC) in the interconnection.

4.6.3	Priorities

(1)	Priorities for an ERCOT System Black Start recovery are listed below:

(a)	Secure and/or stabilize generating units where necessary.

(b)	Prepare Cranking Paths and Synchronization Corridors as necessary to support restoration.

(c)	Assess ERCOT System condition, and available communication facilities.

(d)	Restore and maintain communication facilities to the extent possible.

(e)	Bring units with contracted Black Start capability On-Line.

(f)	Provide service to critical facilities:

(i)	Provide station service for nuclear generating facilities;

(ii)	Provide critical power to as many Generation Resources as possible to prevent equipment damage;

(iii)	Secure or provide startup power for Generation Resources that do not have Black Start capability; and

(iv)	Supply station service to critical substations where necessary.

(g)	Connect Islands at designated synchronization points taking care to avoid recurrence of a Partial Blackout or Blackout of the ERCOT System.

(h)	Restore service to critical Loads such as:

(i)	Military facilities;

(ii)	Facilities necessary to restore the electric utility system, including fuel sources;

(iii)	Law enforcement organizations and facilities affecting public health; and

(iv)	Public communication facilities.

(i)	Restore service to the remaining Customers.  Attention should be given to restoring feeders with under-frequency relay protection.

4.6.4	Responsibilities

(1)	ERCOT’s responsibilities are as follows:

(a)	Shall maintain a Black Start plan in accordance with North American Electric Reliability Corporation (NERC) Reliability Standards and no more than 30 days after revising the Black Start plan, shall notify the TOs of the revised Black Start plan and post the plan with an effective date on the Market Information System (MIS) Certified Area for TOs;

(b)	Shall, no more than 30 days after receiving a TO’s new or revised Black Start plan, notify the TO of ERCOT’s approval or disapproval of the TO’s new or revised Black Start plan and post the approved TO’s new or revised Black Start plan with an effective date on the MIS Certified Area to specified Market Participants requested by the TO;

(c)	Coordinate and approve Planned Outage schedules for contracted Black Start Resources;

(d)	Train TOs, QSEs, and Resource Entities that represent Black Start Resources in the restoration of the ERCOT System.  This training will cover the theory of restoration and the processes that will need to be implemented during a Partial Blackout or Blackout;

[NOGRR194: Replace paragraph (d) above with the following upon system implementation of NPRR857:] (d) Train TOs, QSEs, Direct Current Tie Operators (DCTOs), and Resource Entities that represent Black Start Resources in the restoration of the ERCOT System. This training will cover the theory of restoration and the processes that will need to be implemented during a Partial Blackout or Blackout;

(e) 	Will review the plans and procedures for consistency and conformance with these Operating Guides and ensure that they are updated at least annually;

(f) 	ERCOT shall report to the Reliability and Operations Subcommittee (ROS) by April 1 of each year a plan for review and any testing activities of Black Start Resources;

(g) 	Shall verify that the number, size, and location of Black Start Resources are sufficient to meet the ERCOT Black Start Plan; and

(h)	In the event of a Partial Blackout or Blackout of the ERCOT System, ERCOT shall:

(i)	Maintain continuous surveillance of the status of the ERCOT System;

(ii)	Act as a central information collection and dissemination point for the ERCOT Region;

(iii)	Coordinate reconnection of transmission;

(iv)	Direct assistance for QSEs who represent Black Start Resources, TOs, Resource Entities, and Market Participants;

(v)	Direct the distribution of reserves; and

(vi)	Coordinate the return of the ERCOT System to AGC.

(2)	TOs’ responsibilities are as follows:

(a)	Shall review and submit their Black Start plans to ERCOT via secured webmail or encrypted data transfer:

(i)	Annually by November 1 of each year, for the upcoming calendar year.  Plans submitted before November 1 will be deemed to have been received on November 1 for ERCOT to initiate the approval process described in paragraph (1)(b) above; and

(ii)	When the Black Start plan for the current year has changed.

The TO may request that ERCOT post the TO’s new or revised Black Start plan on the MIS Certified Area for specified Market Participants. The TO will have the responsibility to notify specified Market Participants that the new or revised Black Start plan has been posted on the MIS Certified Area; and

(b)	In event of a Partial Blackout or Blackout of the ERCOT System:

(i)	Shall communicate with local Black Start Resources and the Black Start Resource’s QSE;

(ii)	Coordinate switching to next start Resources and local Load;

(iii)	Shall implement its local Black Start plan;

(iv)	Shall follow the direction of ERCOT on behalf of represented Transmission Service Providers (TSPs) and Distribution Service Providers (DSPs);

[NOGRR177: Replace paragraph (iv) above with the following upon system implementation of NPRR857:] (iv) Shall follow the direction of ERCOT on behalf of represented Transmission Service Providers (TSPs), DCTOs, and Distribution Service Providers (DSPs);

(v)	Shall act as the regional ERCOT representative in coordinating interconnection of Resources; and

(vi)	Shall follow the direction of ERCOT for reconnection of Islands.

(3)	QSEs’ representing Black Start Resources responsibilities are as follows:

(a)	Verify that associated QSE personnel are proficient in implementation and use of the appropriate procedures for use in the event of a Partial Blackout or Blackout; and

(b)	In the event of a Partial Blackout or Blackout of the ERCOT System, QSEs representing Black Start Resources shall:

(i)	Take immediate steps to initiate and maintain communications with its Black Start Resources;

(ii)	Supply ERCOT and/or the local TO with information on the status of generation, fuel, transmission, and communication facilities;

(iii)	Follow the direction of the local TO or ERCOT in regards to output of its Generation Resources; and

(iv)	Provide available assistance as directed by ERCOT or the local TO.

(4)	Black Start Resources’ responsibilities are as follows:

(a)	Verify that associated Resource personnel are proficient in the implementation and use of appropriate individual plant start-up procedures for use in the event of a Partial Blackout or Blackout; and

(b)	In the event of a Partial Blackout or Blackout of the ERCOT System, Black Start Resources shall:

(i)	Isolate the Black Start Resource from the ERCOT Transmission Grid;

(ii)	Establish communications with the local TO who is the primary contact for the Black Start Resource;

(iii)	Supply the local TO and QSE with information on the status of generation, fuel, transmission isolation, and communication facilities;

(iv)	Follow the appropriate plant start-up procedures and request synchronization and auxiliary Load pickup from the TO; and

(v)	Follow the direction of the local TO or ERCOT until such time as normal system operations resume.  The Black Start Resource should follow the direction of the QSE instructed by the TO or ERCOT when necessary.

(5)	Generation Resources that are not Black Start Resources have the following responsibilities in the event of a Partial Blackout or Blackout of the ERCOT System:

(a)	Take immediate steps to initiate and maintain communications with its QSE; and

(b)	Follow the direction of the local TO or ERCOT until such time as normal system operations resume.  The Generation Resource should follow the direction of the QSE as instructed by the TO or ERCOT when necessary.

(6)	Section 8, Attachment A, Detailed Black Start Information, and Section 8, Attachment E, Black Start Plan Template, provide a detailed and specific Black Start information guide.  Interested parties should use this information for technical reference material, Black Start testing, development of Black Start plans, and training of personnel.

4.6.5	Black Start Emergency Back Up Communication Facilities Criteria

(1)	All back-up communications systems shall meet the following minimum requirements:

(a)	Be operational for 72 hours immediately following the start of a Blackout without external power from the ERCOT System;

(b)	Provide direct voice communications between Black Start Resource and TO, TO and other appropriate TOs, and TO and ERCOT; and

(c)	Maintain written procedures that address operator training and the testing of the communication system;

(2)	TOs shall have a satellite phone that meets the minimum back up communication requirements as a back-up communication system and that is compatible with ERCOT’s satellite phone.

4.7       Geomagnetic Disturbance Operating Plan

4.7.1	Monitoring and Dissemination of Space Weather Information

(1)	ERCOT shall maintain procedures to receive Geomagnetic Disturbance (GMD) alerts and warnings issued by the National Oceanic and Atmospheric Administration (NOAA).

(2)	ERCOT shall implement and maintain procedures to provide GMD alerts and warnings to Transmission Operators (TOs).

(3)	Other forecasted and current space weather information is publicly available directly through the NOAA website.

4.7.2	Development and Submission of TO GMD Operating Procedures or Processes

(1)	Each TO that operates transmission equipment that includes a power transformer with a high side wye-grounded winding with terminal voltage greater than 200 kV shall develop a GMD operating procedure or process to mitigate the effects of GMD events on the reliable operation of its system.

(2)	Each TO GMD operating procedure or process shall be provided to ERCOT as soon as practicable but no later than November 25, 2014.  Updates to the plan shall be provided to ERCOT by March 15 of each subsequent year.

(3)	Each TO GMD operating procedure or process shall include:

(a)	A procedure to receive GMD alerts and warnings from ERCOT;

(b)	A description of operational actions the TO intends to take to mitigate the effects of a GMD event.  This description shall include:

(i)	The triggering event for each action;

(ii)	A detailed explanation of each operational action;

(iii)	A list of Entities with which the TO must coordinate, if any, including any actions requested of other Entities in the ERCOT Region in order to implement the TO’s GMD operating procedure or process; and

(iv)	The conditions under which each action would be terminated.

(c)	A procedure for reporting to ERCOT any unusual operational information that could be the result of GMD, such as high reactive loading, MVAr or voltage swings, high geomagnetically induced current on monitored transformers or equipment malfunctions.

4.7.3	ERCOT’s GMD Operating Plan and ERCOT Review of TO GMD Operating Procedures or Processes

(1)	ERCOT shall develop a GMD operating plan and post it on the Market Information System (MIS) Certified Area for TOs.

(2)	The ERCOT GMD operating plan shall coordinate the TO GMD operating procedures or processes.  This coordination is intended to ensure the TO GMD operating procedures or processes are not in conflict with one another and is not intended to be a review of the technical aspects of the TO GMD operating procedures or processes.

(3)	In preparing the ERCOT GMD operating plan, ERCOT shall identify and notify the relevant TOs of any conflicts between the different TO GMD operating procedures or processes and any unacceptable actions requested of ERCOT in the TO operating procedures or processes.

(a)	ERCOT and the TOs shall coordinate development of any required modifications to the TO GMD operating procedures or processes necessary to resolve these conflicts or unacceptable actions.

(b)	A TO shall make the resulting modifications to its GMD operating procedures or processes.

(4)	The ERCOT GMD operating plan shall include:

(a) 	A description of activities designed to mitigate the effects of GMD events on the reliable operation of the interconnected transmission system; and

(b)	Any operating actions required of ERCOT by the TO GMD operating procedures or processes and approved by ERCOT for inclusion in the ERCOT GMD operating plan.

4.8	Responsive Reserve Service During Scarcity Conditions

(1)	This Section details how Responsive Reserve (RRS) service may be manually deployed, also referred to as release of High Ancillary Service Limit (HASL), during scarcity conditions, pursuant to Protocol Section 6.5.7.6.2.2, Deployment of Responsive Reserve (RRS).  The existing measure of scarcity is Physical Responsive Capability (PRC) and spinning reserves.  If PRC and spinning reserves drop below 3,000 MW, this process may be used.  Scarcity conditions may occur during the Peak Load Season when ERCOT System Load is above 60,000 MW.  For all other months, they could occur when ERCOT System Load is above 50,000 MW.

[NOGRR187: Replace paragraph (1) above with the following upon system implementation of NPRR863:] (1) This Section details how Responsive Reserve (RRS) service may be manually deployed, also referred to as release of High Ancillary Service Limit (HASL), during scarcity conditions, pursuant to Protocol Section 6.5.7.6.2.2, Deployment of Responsive Reserve (RRS). The existing measure of scarcity is Physical Responsive Capability (PRC). If PRC drops below 3,000 MW, and all available ERCOT Contingency Reserve Service (ECRS) (dispatchable by Security-Constrained Economic Dispatch (SCED)) and Non-Spinning Reserve (Non-Spin) Service has been deployed, this process may be used. Scarcity conditions may occur during the Peak Load Season when ERCOT System Load is above 60,000 MW. For all other months, they could occur when ERCOT System Load is above 50,000 MW.

4.8.1	Responsive Reserve Service Manual Deployment

(1)	RRS for capacity may be manually deployed (HASL released) when the system approaches scarcity conditions so that the capacity reserved behind HASL will be released to Security-Constrained Economic Dispatch (SCED). The capacity may be released under any of the following conditions:

(a)	When HASL – (Gen + 5 minute load ramp) <= 200 MW, deploy a portion of the available RRS capacity from Generation Resources and Controllable Load Resources after all the available Non-Spinning Reserve (Non-Spin) service has been deployed;

(b)	Additional RRS capacity from Generation Resources and Controllable Load Resources may be deployed, as available, when HASL – (Gen + 5 minute load ramp) <= 200 MW and Resources have responded to any earlier deployments; or

(c)	When PRC <= 2,000 MW, release all remaining RRS capacity from Generation Resources and Controllable Load Resources after all the available Non-Spin has been deployed.

[NOGRR187 and NOGRR191: Replace applicable portions paragraph (1) above with the following upon system implementation of NPRR863 or NPRR939:] (1) RRS for capacity may be manually deployed (HASL released) when the system approaches scarcity conditions so that the capacity reserved behind HASL will be released to SCED. (a) When HASL – (Gen + 5 minute load ramp) <= 200 MW, ERCOT may deploy a portion of the available RRS capacity from Generation Resources and Controllable Load Resources in 500 MW increments after all the available ECRS (dispatchable by SCED) and Non-Spinning Reserve (Non-Spin) service has been deployed and Resources have not responded to any earlier deployments. (b) When HSL – (Gen + 5 minute load ramp) <= 500 MW, ERCOT may deploy Load Resources controlled by high-set under-frequency relays providing RRS.

4.8.2	Responsive Reserve Service Manual Recall

- The manual deployment of RRS for capacity from Generation Resources and Controllable Load Resources may be recalled when HASL – (Gen + 5 minute load ramp) > 1,600 MW and/or PRC >= 3,300 MW.

(2)	The operator will consider system conditions and Ancillary Services in releasing or recalling RRS.  System frequency, load ramp, and factors such as Regulation Up Service (Reg-Up) versus Regulation Down Service (Reg-Down) deployment status will be considered.