## Slide 1
Nov 06, 2019
WMS
ERCOT Staff
Proposed Ancillary Service Methodology for 2020
Preliminary Quantities

## Slide 2: Schedule for Stakeholder Discussion
Sep 11, 2019 – PDCWG (Visit 1)
Sep 16, 2019 – WMWG (Visit 1)
Sep 19, 2019 – OWG (Cancelled)
  Feedback to change Responsive Reserve quantities using an updated Resource Contingency Criteria (RCC) of 2805 MW.
Oct 09, 2019 – PDCWG (Visit 2)
Oct 17, 2019 – OWG
Oct 21, 2019 – WMWG (Visit 2)
Nov 06, 2019 – WMS
Nov 07, 2019 – ROS
Nov 20, 2019 – TAC
Dec 10, 2019 – BOD

## Slide 3: Scope of Discussion
ERCOT is not proposing any changes to the methodologies for determining Ancillary Service (A/S) quantities for 2020.
  Based on feedback received Responsive Reserve quantities for 2020 will be computed using an updated Resource Contingency Criteria (RCC) of 2805 MW.
  The A/S quantities for 2020 contained in this presentation are based on the methodology that was approved in December 2018.
  These quantities reflect moving forward the historic data on which these are based, unless otherwise noted.
A redline version of the draft methodology and spreadsheets that contain the associated quantities for January through September of 2020 have been posted on the meeting page for this meeting.

## Slide 4
Regulation

## Slide 5: Regulation Service Methodology – 2020
The preliminary Regulation quantities for January 2020 thru September 2020 in subsequent slides have been computed using current methodology (2018 and 2019 five-minute net load variability) and updated Wind Adjustment tables.

## Slide 6: Regulation Adjustment Tables

## Slide 7: Hourly Average Regulation Comparison

## Slide 8
Responsive Reserve Service

## Slide 9: Responsive Service Methodology (RRS) - 2020
The preliminary RRS quantities for January 2020 thru September 2020 in subsequent slides have been computed using 2018 and 2019 system inertia conditions and an updated RRS table.
The RRS table tracks RRS requirements for different inertia conditions.
  This table has been updated for 2020. For the update a Resource Contingency Criteria of 2805 MW in associated studies.

## Slide 10: RRS Table - 2020
 | Scenario 1 | Scenario 2 | Scenario 3 | Scenario 4 | Scenario 5 | Scenario 6 | Scenario 7 | Scenario 8 | Scenario 9 | Scenario 10 | Scenario 11 | Scenario 12
LR/PFR | 2.35:1 | 2.2:1 | 2.06:1 | 1.94:1 | 1.83:1 | 1.74:1 | 1.65:1 | 1.58:1 | 1.51:1 | 1.44:1 | 1.39:1 | 1.33:1
Inertia (GW∙s) | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 | 220 | 230 | 240
PFR Req. (no LR) (MW) | 5960 | 5563 | 5200 | 4892 | 4622 | 4329 | 4114 | 3920 | 3744 | 3522 | 3314 | 3139
*RRS (MW) | 3293 | 3234 | 3178 | 3128 | 3086 | 2998 | 2959 | 2908 | 2868 | 2797 | 2707 | 2645
 | Scenario 13 | Scenario 14 | Scenario 15 | Scenario 16 | Scenario 17 | Scenario 18 | Scenario 19 | Scenario 20 | Scenario 21 | Scenario 22 | Scenario 23 | Scenario 24 | Scenario 25
LR/PFR | 1.28:1 | 1.24:1 | 1.19:1 | 1.15:1 | 1.12:1 | 1.08:1 | 1.04:1 | 1.01:1 | 1:1 | 1:1 | 1:1 | 1:1 | 1:1
Inertia (GW∙s) | 250 | 260 | 270 | 280 | 290 | 300 | 310 | 320 | 330 | 340 | 350 | 360 | 370
PFR Req. (no LR) (MW) | 3004 | 2890 | 2784 | 2686 | 2595 | 2510 | 2421 | 2353 | 2290 | 2230 | 2173 | 2119 | 2068
*RRS (MW) | 2598 | 2553 | 2523 | 2486 | 2440 | 2409 | 2372 | 2341 | 2290 | 2230 | 2173 | 2119 | 2068
*RRS quantity is calculated with limit of 60% limit on LRs.
**Red font in table above identifies study scenario where RRS needed < 2300 MW. 2300 MW floor will be used in RRS requirement determination.
***Generation mix (CCs, Gas, SC, Coal, Steam) providing 1150 MW of PFR has been aligned with actual historic system operations.
Inertia < 250 GW·s: 30% Coal + 70% Rest. Inertia ≥ 250 GW·s: 15% Coal + 85% Rest

## Slide 11: RRS January

## Slide 12: RRS February

## Slide 13: RRS March

## Slide 14: RRS April

## Slide 15: RRS August

## Slide 16: Hourly Average RRS Comparison

## Slide 17
Non Spin Reserve

## Slide 18: Non Spinning Reserve Methodology (Non-Spin) - 2020
The preliminary Non-Spin quantities for January 2020 thru September 2020 in subsequent slides have been computed using current methodology (2017, 2018 and 2019 Net load and Net load Forecast) and updated Wind Over-Forecast Error Adjustment tables.

## Slide 19: Wind Over-Forecast Error Adjustment Table - 2020
Wind Over-Forecast Error Adjustment Table track estimated increase in wind over forecast error per 1000 MW increase in installed Wind capacity.
  This table has been updated for 2020.
Average hourly increase in Wind Forecast error per 1000 MW increase in installed Wind capacity = 40 MW
Notes: Average Hourly increase in 2018 = 45 MW

## Slide 20: Non-Spin January

## Slide 21: Non-Spin March

## Slide 22: Non-Spin July

## Slide 23: Non-Spin August

## Slide 24: Hourly Average Non-Spin Comparison

## Slide 25
Discussion