|  |  |  |  |
| --- | --- | --- | --- |
| Key Topic Concept (KTC) Number | 5 | KTC Title | Single Model Energy Storage Resource Energy Deployment Performance (ESREDP) |
| Date Posted | | November 6, 2019 | |
|  | |  | |
| Executive Summary | | This KTC recommends performance metrics and tolerances for measuring Energy Storage Resources (ESRs) ability to follow ERCOT instructions. | |
| Recommendation Description | | ESR performance will be scored using ESR Energy Deployment Performance (ESREDP) % and ESREDP MW. The tolerance for ESREDP is recommended to be the greater of 5 % or 5 MW. | |
| BESTF Discussion | | On 11/04/19, ERCOT staff presented material related to proposed ESREDP calculations. | |
| TAC Action Requested | | None. | |
| TAC Action Summary | |  | |

|  |
| --- |
| Proposed KTC Recommendation Language |

# *Key Topic/Concept recommendation Language for TAC Approval*

None

# *Key Topic/Concept recommendation Language Previously Approved by tac*

None

# *Key Topic/Concept recommendation Language IN DISCUSSION AT BESTF*

1. Energy Storage Resource (ESR) performance will be scored using ESR Energy Deployment Performance (ESREDP) % and ESREDP MW, using the same formulas that apply to Generation Resource Energy Deployment Performance (GREDP) % and GREDP MW.

ATPF = Average Telemetered Power Flow

ARI = Average Regulation Instruction

AEPFR = Average Estimated Primary Frequency Response

ABP = Average Base Point

1. New performance threshold variables, V % and W MW, as specified in ERCOT comments to NPRR 963 submitted on 10/11/2019, will continue to be used for Single Model ESRs and will initially be set to V = 5% and W = 5 MW.
2. Like GREDP, a passing interval must have an ESREDP less than the greater of V % or W MW. Intervals that will be excluded from scoring will also match those intervals excluded from GREDP scoring.

# *Future Decision Points and Issues for Developing Key topic/Concept recommendation Language*

None.

|  |  |
| --- | --- |
| Applicable Protocol Section(s) |  |
| Impacted System(s) / Application(s) |  |