## Slide 1
Final GIC Flows for the Benchmark and Supplemental GMD Events
Minnie Han
November 15, 2019
PGDTF Meeting

## Slide 2: Disclaimer
Final GIC flow results were posted on November 8, 2019.

## Slide 3: Benchmark Event - GIC Flow Summary
There were no transformers with a maximum effective GIC flow above the 75 A per phase threshold.
There was one transformer with a maximum effective GIC flow above 65 A per phase.
The majority of the transformers had maximum GIC flows below 10 A per phase.

## Slide 4: Maximum Effective GIC Distribution: Benchmark Event for 2022 Summer Peak Case
These numbers reflect the percentage of transformers with maximum effective GIC flows in the specified ranges.
Chart: Maximum Effective GIC Flow Distribution
| 0-10 | 11-20 | 21-30 | 31-40 | 41-50 | 51-60 | 61-70
 | 90.7154 | 8.067 | 0.98935 | 0.15221 | 0 | 0 | 0.076104

## Slide 5: Maximum Effective GIC Distribution: Benchmark Event for 2022 Minimum Load Case
These numbers reflect the percentage of transformers with maximum effective GIC flows in the specified ranges.
Chart: Maximum Effective GIC Flow Distribution
| 0-10 | 11-20 | 21-30 | 31-40 | 41-50 | 51-60 | 61-70
 | 90.6535 | 8.1307 | 0.98784 | 0.15198 | 0 | 0 | 0.075988

## Slide 6: Supplemental Event – GIC Flow Summary
There was one transformer with a maximum effective GIC value above 85 A per phase.
    Deadline for thermal assessment is May 8, 2021.
Most of the transformers had a maximum effective GIC value less than 50 A per phase—the majority of those being below 10 A per phase.

## Slide 7: Maximum Effective GIC Distribution: Supplemental Event for 2022 Summer Peak Case
These numbers reflect the percentage of transformers with maximum effective GIC flows in the specified ranges.
Chart: Maximum Effective GIC Flow Distribution
| 0-10 | 11-20 | 21-30 | 31-40 | 41-50 | 51-60 | 61-70 | 71-80 | 81-90 | 91-100
 | 85.3077 | 10.6154 | 3.0769 | 0.69231 | 0.23077 | 0 | 0 | 0 | 0 | 0.076923

## Slide 8: Maximum Effective GIC Distribution: Supplemental Event for 2022 Minimum Load Case
These numbers reflect the percentage of transformers with maximum effective GIC flows in the specified ranges.
Chart: Maximum Effective GIC Flow Distribution
| 0-10 | 11-20 | 21-30 | 31-40 | 41-50 | 51-60 | 61-70 | 71-80 | 81-90 | 91-100
 | 85.1767 | 10.5991 | 3.2258 | 0.61444 | 0.30722 | 0 | 0 | 0 | 0 | 0.076805

## Slide 9
Questions?