## Slide 1
Regulation Bias Analysis Post SCR-773
Oct 2019
ERCOT
Operations Planning
PDCWG | November 11th, 2019

## Slide 2
Discussion Points
Current GTBD Parameters & References
Metric to measure Regulation bias and performance
Regulation Deployed comparison for last three months.
Total Regulation (net) Deployed Comparison
Regulation Deployed 15-minute interval comparison by each hour for 2017, 2018, and 2019 months
Regulation Exhaustion Rate
Regulation bias for consecutive 5-min SCED intervals
Time Error & Contributing Factors
Summary

## Slide 3: Current GTBD Parameters
Notes: 3/12/18 – Integral ACE Time Constant Changed from 60 min to 45 min
5/17/18 - K4 Changed from 0.3 to 0.2 and K5 Changed from 0.4 to 0.5
12/4/18 - K6 Changed from 0 to 0.5
2/12/19 - K6 Changed from 0.5 to 1
4/01/19 - K5 changed from 0.5 to 0.4 and Max. Integral ACE Feedback changed from 250 to 150
4/24/19 - Max. Integral ACE Feedback changed from 150 to 160. PWRR Threshold changed from 20 to 25.
5/22/19 – K5 changed from 0.4 to 0.5 Max. Integral ACE Feedback changed from 160 to 200. PWRR Threshold changed from 25 to 30.

## Slide 4: Projected Wind Ramp Rate MAE

## Slide 5: Projected Wind Ramp Rate Error

## Slide 6: References

## Slide 7
Metrics to Measure SCR-773 Performance
Trend and monitor the regulation deployed by hour.
Set target of 50 MW for total regulation deployed by hour for peak hours.
Set target of 85% for the number of intervals where regulation deployment was both up and down for peak hours.
Track the Regulation exhaustion rate for all hours (not to exceed 5%).
Using a 50MW filter, target 15 occurrences or less per month for regulation bias of six or more consecutive 5 minute intervals for peak hours.

## Slide 8: Total Regulation Deployed Comparison
Total regulation deployed for the last three months.

## Slide 9: Total Regulation Deployed Comparison - Monthly

## Slide 10: Metric 1: Regulation Deployed Comparisons
Trend and monitor the regulation deployed by hour.

## Slide 11: Regulation Deployed Comparison

## Slide 12: Regulation Deployed Comparison

## Slide 13: Regulation Deployed Comparison

## Slide 14: Metric 2: Total Regulation Deployed Comparisons
Set target of 50MW for total regulation deployed by hour for peak hours.

## Slide 15: Total Regulation Deployed Comparison

## Slide 16: Metric 3: 15-min Intervals Where Both REGUP/REGDN Were Deployed
Set target of 85% for the number of intervals where regulation deployment was both up and down.

## Slide 17: “Zero” Crossing Regulation

## Slide 18: “Zero” Crossing Regulation

## Slide 19: Metric 4: Regulation Exhaustion Rate
Track the regulation exhaustion rate for all hours (not to exceed 5%.)

## Slide 20: Regulation Exhaustion Rate

## Slide 21: Regulation Exhaustion Rate

## Slide 22: Metric 5: Stats on REGUP Bias for Consecutive 5-min Intervals
Using a 50MW filter, target 15 occurrences or less per month for regulation bias of six or more consecutive 5-minute intervals for peak hours.

## Slide 23: Regulation Bias for Consecutive SCED Intervals

## Slide 24: Regulation Bias for Consecutive SCED Intervals

## Slide 25: Time Error and Contributing Factors
Accumulated Time Error, Load and Wind Ramp, PWRR Error, Start-Up/Shut-Down Hours, STLF Error, and Expected Generation Deviation.

## Slide 26: Time Error Accumulation

## Slide 27: Load Profile

## Slide 28: Net Load Profile

## Slide 29: Load Ramp

## Slide 30: Wind Profile

## Slide 31: Start-Up & Shut-Down Hours

## Slide 32: Short-Term Load Forecast Error

## Slide 33: STLF Error Chart
Chart: STLF Error
Notes: Min,Max, 10th, 90th percentile
15 minute intervals

## Slide 34: Expected Generation Deviation

## Slide 35: Expected Generation Deviation
Chart: Expected Generation Deviation by Resource Type
Cogen | -0.71773 | 13.79 | 15.0879 | 8.3537 | 11.3613 | -0.80953 | -17.3764 | -4.1233 | -12.3324 | -27.9286 | -21.2057 | -28.0843 | -28.8423 | -29.8133 | -37.6117 | -29.2597 | -21.2756 | -8.7901 | -22.1951 | -16.3321 | -4.7995 | -8.2606 | -2.2153 | 7.4376
Nuclear | 2.9018 | 3.2859 | 3.4649 | 3.1238 | 2.7921 | 3.1158 | 3.2972 | 3.3983 | 3.4608 | 3.4876 | 3.6976 | 3.2009 | 3.0443 | 2.7705 | 2.5303 | 2.5719 | 2.0978 | 2.0517 | 2.6046 | 3.0947 | 2.7136 | 2.3407 | 3.3502 | 2.7636
Gas Turbine | 3.9242 | 1.397 | 1.0116 | 0.96318 | 2.0844 | 4.7724 | 2.088 | 2.281 | 4.1005 | 7.6222 | 3.6942 | 3.584 | -1.4725 | -3.6581 | -2.0206 | 0.15716 | -3.8559 | -3.5495 | -4.7853 | -1.2779 | 1.4889 | 5.608 | 7.3377 | 7.3467
Steam | 0.65844 | 0.60389 | 0.53703 | 0.045854 | -2.5132 | -2.2732 | -0.15798 | 0.014839 | -0.54886 | -1.1479 | -1.1153 | -1.264 | 0.28762 | -0.68221 | 0.70092 | 0.49673 | 1.8608 | 1.5496 | 2.7613 | 0.016034 | 3.3982 | 2.5925 | 2.2858 | 1.0403
Fossil | -0.80015 | 15.1216 | 9.8555 | 12.8266 | 2.83 | -19.624 | -32.3217 | -0.95635 | -8.8109 | -14.1962 | -8.2944 | -14.8609 | -25.4979 | -28.0796 | -34.1636 | -26.2898 | -18.4973 | -18.1503 | -26.5573 | -3.197 | 12.7784 | 24.9526 | 37.1292 | 29.7374
Wind | -3.2636 | -20.1194 | -9.6421 | -25.3917 | -28.4245 | -32.1912 | -27.6558 | -32.9241 | -97.2877 | -51.8075 | 0.84694 | -40.8799 | -30.8475 | -13.2688 | -1.7549 | 17.5545 | 28.8939 | 19.3066 | -5.8459 | 84.6208 | 105.3628 | 59.9386 | 16.116 | -0.51154
Hydro | 0.18113 | 0.56376 | -0.014647 | 0.028321 | 0.0059676 | -0.0083778 | 1.3421 | 0.551 | 0.49241 | 0.09316 | 2.7268 | 0.12401 | 0.58772 | 1.7398 | 0.37577 | 0.29446 | 0.013055 | -0.38024 | -0.070568 | -0.55455 | -1.4999 | -0.099534 | -0.13363 | 0.15145
PVGR | 0.00041937 | 0 | 0.00046718 | 0.00040504 | 0 | 0.00010173 | 0.00082755 | 0.24215 | 35.5835 | 47.0575 | 13.6479 | 8.1226 | 3.9213 | 4.8761 | 1.2791 | -0.3291 | -7.8723 | -34.7027 | -58.8298 | -3.0817 | 0.0018907 | 0.0016381 | 0.00098703 | 0.00022895

## Slide 36: Expected Generation Deviation
Chart: Exp Gen Deviation by Renewable vs Non-Renewable
Renewable | -3.2632 | -20.1194 | -9.6417 | -25.3913 | -28.4245 | -32.1911 | -27.655 | -32.6819 | -61.7042 | -4.75 | 14.4949 | -32.7573 | -26.9262 | -8.3926 | -0.47589 | 17.2254 | 21.0216 | -15.3961 | -64.6757 | 81.5391 | 105.3647 | 59.9402 | 16.117 | -0.51131
Non-Renewable | 6.1477 | 34.7622 | 29.9422 | 25.3415 | 16.5606 | -14.8269 | -43.1288 | 1.1655 | -13.6385 | -32.0698 | -20.4968 | -37.3003 | -51.8929 | -57.7229 | -70.1889 | -52.0293 | -39.6571 | -27.2689 | -48.2423 | -18.2509 | 14.0798 | 27.1336 | 47.754 | 48.4771

## Slide 37: Questions?
Thank you!