## Slide 1
Potential Price Correction: Incorrect Electrical Bus Shift Factors in the Real-Time Market
David Maggio
TAC
November 20, 2019

## Slide 2: Background-Timeline
October 16, 2019 – A system enhancement was deployed for the calculation of Electrical Bus Shift Factors in the Real-Time market (RTM)
  Enhancement intended to align the calculation of Electrical Bus Shift Factors when an Electrical Bus is energized in base case but disconnected by a contingency.
  As it is not specifically defined in Protocol, during the discussion of NPRR833, Modify PTP Obligation Bid Clearing Change, it was agreed that an Electrical Bus’s Shift Factor for a specific constraint should be set to “0” if the contingency related to the constraint disconnects that Electrical Bus .
    Note that this process doesn’t affect the application of the “pickup” Shift Factor to Resource Nodes when the physical Resource and Resource Node are both disconnected by a contingency.
  The need for enhancement: Prior to the change, the Shift Factor of an Electrical Bus connecting a Generation Resource was assigned a non-zero “pickup” Shift Factor if the Generation Resource was energized in the base case, but disconnected by a contingency.
  Software Error – The system inadvertently set all Shift Factors associated with that Electrical Bus to “0” if any active contingency disconnected an Electrical Bus. As a result, the Shift Factors for some Electrical Buses were incorrectly set to “0” and used in downstream applications.
    October 21, 2019 – ERCOT became aware of the software error, began investigating RTM prices, and implemented an emergency patch.
October 23, 2019 – ERCOT issued RTM price correction for OD October 21, 2019
October 24, 2019 – ERCOT issued Market Notice M-A102419-01

## Slide 3: Background – Constraint with Disconnected Electrical Buses
G
Station A
Station B
Station C
Station D
EB2
UNIT_G1
EB1
EB3
EB4
EB5
Line contingency SAB2
Overloading
X
X
X
Contingency SAB2 is the loss of line LN2 from station A to station B, which disconnects the Electrical Buses EB1 ~ EB5.
LN1
LN2

## Slide 4: Background – Electrical Bus Shift Factor
For each SCED interval, Electrical Bus Shift Factors are calculated in EMS and then transferred to MMS. Each Electrical Bus Shift Factor is calculated per constraint and per Electrical Bus where a constraint is defined as a pair of a contingency and a piece overloaded equipment.
Example:
Assuming two constraints are active for a SCED interval, constraint SAB2:LN1 disconnects the Electrical Buses EB1~EB5, while the other constraint SCD1:LN8 does not disconnect any Electrical Bus.
Prior to system Enhancement:
SCED Interval | CONTINGENCY | OVERLOAD | EB NAME | Shift Factor
… |  |  |  | 
10/1/2019 10:35 | SAB2 | LN1 | EB1 | 0
10/1/2019 10:35 | SAB2 | LN1 | EB2 | 0
10/1/2019 10:35 | SAB2 | LN1 | EB3 | 0
10/1/2019 10:35 | SAB2 | LN1 | EB4 | 0
10/1/2019 10:35 | SAB2 | LN1 | EB5 | -0.02
… |  |  |  | 
10/1/2019 10:35 | SCD1 | LN8 | EB1 | 0.05
10/1/2019 10:35 | SCD1 | LN8 | EB2 | 0.05
10/1/2019 10:35 | SCD1 | LN8 | EB3 | 0.05
10/1/2019 10:35 | SCD1 | LN8 | EB4 | 0.05
10/1/2019 10:35 | SCD1 | LN8 | EB5 | 0.05
… |  |  |  | 
Should be set to zero to align with other disconnected Electrical buses

## Slide 5: Background – Software Error
The intended enhancement was designed to reset Electrical Bus Shift Factors for only the disconnected Electrical Buses, and for only the constraint where its contingency disconnected the Electrical Buses.
However, the change was incorrectly applied to all Electrical Bus Shift Factors, including Shift Factors for other unrelated constraints.
Post-System Enhancement:
SCED Interval | CONTINGENCY | OVERLOAD | EB NAME | Shift Factor
… |  |  |  | 
10/18/2019 10:35 | SAB2 | LN1 | EB1 | 0
10/18/2019 10:35 | SAB2 | LN1 | EB2 | 0
10/18/2019 10:35 | SAB2 | LN1 | EB3 | 0
10/18/2019 10:35 | SAB2 | LN1 | EB4 | 0
10/18/2019 10:35 | SAB2 | LN1 | EB5 | 0
… |  |  |  | 
10/18/2019 10:35 | SCD1 | LN8 | EB1 | 0
10/18/2019 10:35 | SCD1 | LN8 | EB2 | 0
10/18/2019 10:35 | SCD1 | LN8 | EB3 | 0
10/18/2019 10:35 | SCD1 | LN8 | EB4 | 0
10/18/2019 10:35 | SCD1 | LN8 | EB5 | 0
… |  |  |  | 
The disconnected Electrical Buses Shift Factors for other unrelated constraints were also incorrectly set to “0”

## Slide 6: Impacts
Market Impact: RTM
  SCED dispatch was not impacted. SCED uses Resource Shift Factors rather than Electrical Bus Shift Factors; Resource Shift Factors were not impacted by the error.
  However, RTM prices (Real-Time Settlement Point Prices (RTSPPs) and Real-Time Price for Energy Metered for Resources (RTRMPRs)) were impacted for Operating Days (ODs) 10/16/2019 – 10/21/2019.
Pricing Impact
  ERCOT determined this issue impacted the RTM prices for the ODs.
    ODs 10/16/19 – 10/20/19 – Board Review (December 2019)
    ERCOT will seek ERCOT Board Review (at its December 2019 meeting) of RTM prices in need of correction, in accordance with ERCOT Protocol Section 6.3(6).
    OD 10/21/19 – ERCOT Price Correction
      ERCOT corrected prices for OD 10/21/2019, before prices were final, in accordance with Protocol Section 6.3(5).

## Slide 7: Potential Price Correction (Board Review)
Market: RTM
Impacted ODs: 10/16/19 – 10/20/19
Price Correction Methodology: ERCOT reran the SCED LMP calculation with corrected Electrical Bus Shift Factors, and then recalculated RTSPPs and RTRMPRs.
Estimated Impact: The following slides include a summary of ERCOT’s preliminary study; this data is subject to change. Final data and detailed study results will be included in Board materials prior to the December Board meeting.

## Slide 8: Summary of Price Impacts
* For 10/21/19, corrected RTM prices were posted prior to becoming final.
OD | Number of Impacted Settlement Points | Number of Impacted EPS Meters | Count of Changes in RTSPPs across all Settlement Intervals | Count of Changes in RTRMPRs across all Settlement Intervals
10/16/19 | 4 | 0 | 91 | 0
10/17/19 | 8 | 2 | 235 | 78
10/18/19 | 9 | 3 | 655 | 92
10/19/19 | 9 | 1 | 538 | 43
10/20/19 | 10 | 2 | 717 | 12
10/21/19 * | 10 | 2 | 363 | 45

## Slide 9: RTM Settlement Impacts
 | 10/16 |  | 10/17 |  | 10/18 | 
Energy Imbalance | $60k | 1.3% | $5k | 0.4% | $123k | 2.3%
PTP Obligations | ($54k) | 1.0% | ($8k) | 0.6% | ($91k) | 1.8%
RENA | ($6k) | 0.7% | $3k | 24.7% | ($32k) | 18.9%
Note: The Settlement data provided herein is an estimate; final Settlement amounts may differ.
All Settlement amounts are net amounts due to/from ERCOT. Negative amounts are increased payments to Market Participants; positive amounts are increased charges.
The % amount is the absolute value of the % of impact to the previously settled net amount due to/from ERCOT.

## Slide 10: RTM Settlement Impacts
 | 10/19 |  | 10/20 | 
Energy Imbalance | $286k | 2.5% | $95k | 2.1%
PTP Obligations | ($185k) | 1.8% | ($39k) | 0.8%
RENA | ($101k) | 7.8% | ($56k) | 12.6%
Note: The Settlement data provided herein is an estimate; final Settlement amounts may differ.
All Settlement amounts are net amounts due to/from ERCOT. Negative amounts are increased payments to Market Participants; positive amounts are increased charges.
The % amount is the absolute value of the % of impact to the previously settled net amount due to/from ERCOT.

## Slide 11: Additional material regarding the November 14th Market Notice update

## Slide 12: Background
During review of the RTM Electrical Bus Shift Factor issue, a separate but related software error was identified.
The software intended to capture the list of Electrical Buses that are fully disconnected from the rest of the ERCOT grid under a contingency, also incorrectly included Electrical Buses that are on the end of open-ended transmission equipment under contingency.
After identifying this additional issue, an emergency patch was put into production and ERCOT began investigating price impacts.
ERCOT issued Market Notice M-A102419-02
Impacted ODs:
  ODs 10/16/2019 – 10/21/2019 – no additional pricing impacts
  ODs 10/22/2019, 10/25/2019, 10/27/2019 – 10/28/2019, 11/01/2019 – 11/03/2019, 11/05/2019, and 11/07/2019 – no pricing impacts
  ODs 10/23/2019 – 10/24/2019, 10/26/2019, 10/29/2019 – 10/31/2019, 11/04/2019, and 11/06/2019 – some impacts for certain RTSPPs and RTRMPRs

## Slide 13: Background – Constraint with an Open-Ended Electrical Bus
Station Z
Station X
Station Y
Station W
EB1
Line contingency
Line outage
With the line outage, EB1 remains energized but is on the end of an open-ended transmission line between stations W and Z under the contingency.

## Slide 14: Potential Price Correction (Board Review)
Market: RTM
Impacted ODs: 10/23/2019 – 10/24/2019, 10/26/2019, 10/29/2019 – 10/31/2019, 11/04/2019, and 11/06/2019
Price Correction Methodology: ERCOT reran the SCED LMP calculation with corrected Electrical Bus Shift Factors, and then recalculated RTSPPs and RTRMPRs.
Estimated Impact: The following slides include a summary of ERCOT’s preliminary study; this data is subject to change. Final data and detailed study results will be included in Board materials prior to the December Board meeting.

## Slide 15: RTM Settlement Impacts
 | 10/23 |  | 10/24 |  | 10/26 |  | 10/29 | 
Energy Imbalance | ($24) | - | - | - | ($116) | - | ($34) | -
PTP Obligations | $30 | - | - | - | $32 | - | $29 | -
RENA | ($7) | - | - | - | $85 | 0.2% | $5 | -
Note: The Settlement data provided herein is an estimate; final Settlement amounts may differ.
All Settlement amounts are net amounts due to/from ERCOT. Negative amounts are increased payments to Market Participants; positive amounts are increased charges.
The % amount is the absolute value of the % of impact to the previously settled net amount due to/from ERCOT.

## Slide 16: RTM Settlement Impacts
 | 10/30 |  | 10/31 |  | 11/4 |  | 11/6 | 
Energy Imbalance | ($75) | - | ($83) | - | - | - | ($4) | -
PTP Obligations | $61 | - | $145 | - | - | - | $8 | -
RENA | $14 | - | ($64) | - | - | - | ($4) | -
Note: The Settlement data provided herein is an estimate; final Settlement amounts may differ.
All Settlement amounts are net amounts due to/from ERCOT. Negative amounts are increased payments to Market Participants; positive amounts are increased charges.
The % amount is the absolute value of the % of impact to the previously settled net amount due to/from ERCOT.