## Slide 1
Resource Integration Workshop
Resource Integration Topics
ERCOT
Jay Teixeira
November 21, 2019

## Slide 2: Quarterly Stability Assessment (QSA)
Planning Guide 5.9
Next Deadline for QSA
If a GINR is not included in QSA, its Initial Synchronization date will be automatically delayed to the next quarter
All-Inclusive Generation Resource Initial Synchronization Date | Last Day for an IE to meet prerequisites as listed in paragraph (4) below | Completion of Quarterly Stability Assessment
Upcoming January, February, March | Prior August 1 | End of October
Upcoming April, May, June | Prior November 1 | End of January
Upcoming July, August, September | Prior February 1 | End of April
Upcoming October, November, December | Prior May 1 | End of July

## Slide 3: Quarterly Stability Assessment (QSA)
Planning Guide 5.9, Quarterly Stability Assessment
Issue’s seen in the QSA that had May 1, 2018 deadline
  10 day comment period for FIS
    Needs to be complete before QSA deadline
    TSPs need to plan for it
  Dynamic data validation
    Dependent on FIS Stability study
    Need to meet PG 6.9 15 to 30 days prior to QSA deadline

## Slide 4: Resource Integration and Ongoing Operations – Interconnection Services (RIOO-IS) – Releases
No new functionality releases

## Slide 5: Active PGRR’s
PGRR071 - Update Interconnection Process Timetables to Align with NPRR926 – Goes to TAC on Nov. 20th.
NPRR973 et al – Add Definitions for Generator Step-Up and Main Power Transformer tabled by ROS on Nov 7 and sent NPRR, NOGRR, PGRR, RRGRR to PLWG, with NOGRR196 also being sent to OWG.
PGRR076 – Improvements to Generation Resource Interconnection or Change Request (GINR) Process, ROS Nov. 7 sent to PLWG.

## Slide 6: Change Implementation of “Initial Synchronization” date
ERCOT will change how it implements the definition of Initial Synchronization to be the date when the first repowered turbine will (can) be synchronized
INR will have to meet the QSA deadline for this date to allow new turbines to synchronize after repower
Not allow any new repowered turbines to synchronize before the quarter for the QSA they were studied
Synchronization of new turbines is also dependent on SSR study results

## Slide 7: SSR Study Scope
ERCOT would like TSPs to submit their SSR study scope to ERCOT to get reviewed and approved by ERCOT. Rules will be proposed to make it a requirement.
The SSR study scope should be uploaded to RIOO as “other”.
The SSR scope review will be finished within 10 business days. Feedback will be sent to TSP by email.
SSR study scope guidelines are posted at http://www.ercot.com/services/rq/integration.
This should help on the review of the final SSR Study to gain approval by ERCOT

## Slide 8: PMU Requirements for Repowering Projects
ERCOT is considering requiring PMU installation for repowering projects for the following reasons:
  PMU data needed for model validation;
  PMU data needed for post-event analysis;
  PMU data needed to increase situational awareness, and enable operators to take prompt actions in case of abnormal system behaviors like oscillations;
  PMU data needed for a linear state estimation, as recommended by NERC.

## Slide 9: PMU Requirements for Repowering Projects
Nodal Operating Guide 6.1.3.2
(4) The Facility owner(s), whether a Transmission Facility owner or new Generation Resource owner, shall install phasor measurement recording equipment at the following Facilities.
(a) Flexible AC transmission system devices configured to actively control steady-state voltage or power transfer capability, operated at or above 100 kV, and energized after July 1, 2015;
(b) Within 18 months after receiving written notice from ERCOT, a Transmission Facility identified by ERCOT associated with each published generic transmission constraint as deemed necessary by ERCOT; and
New generating Facilities over 20 MVA aggregated at a single site placed into service after January 1, 2017.
Generators or storage devices placed into service after August 1, 2020 following any modification described in Planning Guide Section 5.1.1(1)(b)

## Slide 10: Payment Returns
ERCOT is having issues with payments made in RIOO to authorize.net being returned
ERCOT will accept wire transfers for money owed due to returns
ERCOT will consider setting INR status to “Suspended” if money not remitted in reasonable time

## Slide 11: Other Topics
Site Control clarification – Suzi McClellan
FIS Stability Report Redaction – Paul Cox
  PG 5.4.8(5) requires that stability study model data and parameters, contingencies causing instability should be redacted from the public version of FIS study reports. Should all contingencies be redacted
SSR Studies – What can be shared with IE – Nick Oberski

## Slide 12: Site Control
Site Control clarification – Suzi McClellan
Other ISO/RTOs outside ERCOT having issues with Site Control as well
  Some reporting that they spend too much time trying to verify adequate acreage for specific type of technology
  Time spent is also used to make sure that a Site is not used for more than one project

## Slide 13: FIS Stability Report Redaction
FIS Stability Report Redaction – Paul Cox
  PG 5.4.8(5) requires “study element(s) report shall not contain sensitive information including, but not limited to, confidential plant design information including stability study model data and parameters and contingencies causing instability. The TSP(s) shall provide this information to ERCOT and other TSP(s) upon request.”
Should these be included?
  Any contingencies, including those not causing instability
  Any plots, including VRT or stability plots
  Any one-lines, including IE or TSP POI one-lines

## Slide 14: SSR Studies – What can be shared with IE
SSR Studies – What can be shared with IE – Nick Oberski
For posting on MIS, data is considered Certified for TSPs only, but SSR studies are not posted on MIS
Currently, no known rules forbid TSP’s sharing data with IE
  TSPs should be careful about:
    Revealing non-public data about nearby generation
    Referring to other generation by name
    Referring to generation sharing a POI
    Referring to stability issues in SSR report

## Slide 15: Other contact information
ResourceIntegrationDepartment@ercot.com is distribution list for Resource Integration department

## Slide 16: Questions?
Thank you!