## Slide 1: Planning Geomagnetic Disturbance Task Force (PGDTF) Update to ROS
December 05, 2019
Aster Amahatsion
2019 PGDTF Chair
<number>
Notes: <number>

## Slide 2: PGDTF Meeting
Business meeting was held on November 15th , 2019
Discussed GIC flow for 2019 GIC cases
    ERCOT posted the final GIC flow results on November 8, 2019 on MIS.
    Transformer’s GIC Flows for GMD Benchmark Event Summary
      There were no transformer with maximum effective GIC flow above 75 A per phase threshold.
      There was one transformer with maximum effective GIC flow above 65 A per phase.
      The majority (90.72%) of the transformers had maximum effective GIC flows below 10 A per phase.
    Transformer’s GIC Flows for Supplemental GMD Event Summary
      There was one transformer with maximum effective GIC value above 85 A per phase. Deadline for the transformer thermal assessment is May 8, 2021.
      Most of the transformers had a maximum effective GIC value less than 50 A per phase, the majority (85%) being below 10 A per phase.
<number>
12/05/2019 ROS Meeting
Notes: <number>

## Slide 3
Discussed GMD Vulnerability Assessment activities
  ERCOT Presented on GMD Vulnerability Assessment targeted milestones.
  These targeted milestones include presenting the GMD Vulnerability Assessment scopes, publish the steady state voltage performance criteria and publishing the benchmark and supplemental GMD Vulnerability Assessment reports.
Next PGDTF meeting: December 10, 2019 at the Met Center (WebEx available)
12/05/2019 ROS Meeting
<number>
PGDTF Meeting

## Slide 4: Questions
<number>
12/05/2019 ROS Meeting
Notes: <number>