## 1) General Information
CenterPoint Energy Distribution Loss Factor for |  |  |  |  | 2020 |  |  |  |  | Color Key
INPUT - Must be changed every year
| ----> Changes for 2020 are shown in bold red font | [9 empty] | Formula - Don’t touch
General Information on Distribution Loss Factor:
The Distribution Loss Factor is a percent that ERCOT will use to determine distribution losses for each Distribution Service Provider.
See ERCOT Protocols Section 13: Transmission and Distribution Losses, which was updated on September 1, 2016. See following
protocol link: http://www.ercot.com/mktrules/nprotocols/current
According to this protocol, ERCOT will calculate Distribution Loss Factors for each Settlement Interval of the Operating Day for
settlement purposes. Distribution Loss Factors will be calculated from the data provided by Distribution Service Providers using
the following equation
SILFi = F1 * (SIELi/AAL) + F2 + F3 / (SIELi / AAL)
Where:
i = interval (15 minutes)
SILFi = Settlement Interval Distribution Loss Factor
SIELi = Settlement Interval estimated ERCOT System Load
AAL = Annual Interval Average ERCOT System Load (15 minute basis)
F1, F2, F3 = Coefficients derived from regression analysis of the TDSP loss study results
AAL = Annual Total System MWh / (Number of settlement intervals in the year) Typically = 365 days * 24 hrs * 4 intervals
AAL value for use in 2020 = 10,740 MWH
AAL value for use in 2019 = 10,708 MWH
AAL value for use in 2018 = 10,190 MWH
AAL value for use in 2017 = 9,898 MWH
AAL value for use in 2016 = 9,940 MWH
AAL value for use in 2015 = 9,741 MWH
AAL value for use in 2014 = 9,290 MWH
AAL value for use in 2013 = 9,304 MWH
AAL value for use in 2012 = 9,463 MWH
AAL value for use in 2011 = 9,034 MWH
AAL value for use in 2010 = 8,785 MWH
AAL value for use in 2009 = 9,043 MWH
Customer Coding for CenterPoint Energy:
Distribution customers that take service at secondary voltage are coded "D"
Distribution customers that take service at primary voltage are coded "E"
CenterPoint Energy customers taking service at transmission level voltages have no distribution losses associated with their energy
delivery. Therefore, each transmission ESI-ID account has been coded with a "T", and their losses are determined by ERCOT rules for
transmission customers.
For "D" Secondary Customers
F1 = |  | 0.0177
F2 = |  | 0.00048
F3 = |  | 0.0202
AAL for ERCOT (15 mins) = 10,708 |  | 10740
For "E" Primary Customers
F1 = |  | 0.01225
F2 = |  | 1e-06
F3 = |  | 0.00045
AAL for ERCOT (15 mins) = 10,708 |  | 10740
Assumptions
1. Assume AAL for CNP corresponds to AAL for ERCOT
2. However, the peak for CNP is proportionately greater than the peak for ERCOT relative to AAL.
Ratio of Peak to AAL
|  | CNP | ERCOT
|  | 2.0042 | 1.7399
Ratio of Peak to AAL for CNP is not proportional to ERCOT
| 2017 for use in 2018 |  | 2018 for use in 2019 |  | 2019 for use in 2020
| 15 mins | 1 hour | 15 mins | 1 hour | 15 mins | 1 hour
CNP Peak | 3789 | 15156 | 3849 | 15396 | 3917.75 | 15671
CNP AAL | 1954.75 | 7819 | 1996.75 | 7987 | 1954.75 | 7819
ERCOT Peak | 17406.75 | 69627 | 18327 | 73308 | 18686 | 74744
ERCOT AAL | 10190 | 40760 | 10708 | 42832 | 10740 | 42960
CNP peak is proportionately higher than CNP AAL as compared to ERCOT peak vs ERCOT AAL, so % losses (and DLF) above AAL are
increased an amount that is consistent with this higher loading at peak, so that when ERCOT hits peak, % losses will correspond to CNP peak.
Methodology upon which the calculation of loss factor was made:
Over the years, CenterPoint Energy has developed system loss equations for each part of the system. Equations for distribution
substation transformer losses, distribution primary conductor losses, distribution transformer losses and secondary conductor losses
were utilized to calculate the total losses on the CenterPoint Energy distribution system for various load levels. See Tab 3 - Loss Equations.
|  | Losses = | AX2 + B
A = Constant
B = Constant
X = Input to System (MW)
The constants (A & B) for each of the equations were updated in 2018 for use in 2019 as follows:
1. Substation Transformer Losses - The A B constants for substation transformers were updated for | [7 empty] | 2020
The current substation transformer database was used to determine the total "No-load" losses for all transformers on the system.
This database contains test data for every substation transformer.
| The total no-load losses are |  | 18.008 MW.
Also, the database provided the total "Load" losses for the transformers on the system at rated trf load.
| This value is | 60.821 MW | at | 18.008 MW | load level.
| This results in a total of |  | 78.829 MW | of substation transformer losses at approximately |  |  |  | 18.076 MW | at CNP (Sub Trf nameplate rating)
The constants in the system loss equations were adjusted to match this result. See Tab 3.
2. Primary Conductor Losses (No change in the A B constants for primary conductor)
The primary conductor losses for 2007 were considered to be similar to the losses in 2006, but the constant for the system loss
equation was increased 2.5% due to the increased loading on our circuits which is a result of our revised design criteria.
The design criteria allows higher loadings due to an increase in switching operations under contingency conditions from
2 pairs of switching operations to 4 pairs of switching operations.
| For | 2020 | there is no further change in the system loss equations.
3. Distribution Transformer Losses - The A B constants for distribution transformers were updated for | [7 empty] | 2020
An inventory of the distribution transformers was downloaded from the GIS system. For every size transformer
the "No-load" losses and "Load" losses were determined by various test reports. This information was entered
for each size of transformer to determine the total "No-load" losses and the total "Load" losses for the distribution transformers.
Additionally, a TLM (Transformer Load Maintenance) Program was used to calculate no-load and load losses.
Since the no-load losses used in the TLM program were based on older/higher values from 1985 and the GIS spreadsheet
used more current test values from 2000-2005, the results of the two programs were averaged together to get
a balanced result for "no-load" losses for a distribution system that has both old and new transformers.
The "load losses" from both methods were very close, so the load losses from GIS were used.
See Tab 3 for the updated A B constants for distribution transformers.
4. Secondary Conductor Losses - No change in the A B constants for secondary conductor for | [6 empty] | 2020
The constant in the system loss equation for secondary losses for 2017 is same as used in previous years.
5. AAL for ERCOT
| The AAL for ERCOT was updated based on information from ERCOT. The new value for | [5 empty] | 2019 is 10,740 MWH |  | for 15 minutes.
DLF Coefficients (F1, F2 and F3)
For both primary and secondary customers, the F1, F2 and F3 coefficients were selected to provide a curve fit with the loss equations that were
developed above. F1 impacts the right side of the curve, F2 impacts the middle/entire curve, and F3 impacts the left side of the curve. These
coefficents were adjusted to get a curve fit in the most critical areas. See spreadsheet and graphs in Tab 2 - Loss Analysis.
The F1, F2, and F3 coefficients for D secondary customers and E primary metered customers for 2017 are shown above.
Overall results:
For "E" Primary Customers |  |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 for use in 2020
|  | DLF at AAL | 1.272% | 1.299% | 1.274% | 1.286% | 1.3% | 1.27%
|  | DLF at ERCOT Peak | 2.05% | 2.159% | 2.154% | 2.107% | 2.155% | 2.157%
For "D" Secondary Customers |  |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 for use in 2020
|  | DLF at AAL | 3.739% | 3.776% | 3.805% | 3.791% | 3.816% | 3.838%
|  | DLF at ERCOT Peak | 4.144% | 4.247% | 4.256% | 4.213% | 4.259% | 4.289%
Questions:
If you have any questions, please call Robert Pitcel at 713-207-7621 or Ben Kirchhofer at 713-207-6173
or email at robert.pitcel@centerpointenergy.com or bennett.kirchhofer@centerpointenergy.com
CenterPoint Energy Distribution Loss Factor For 2020 Rev 1
2019-10-14

## Loss Comparison (hidden)
Loss Comparison With Different A/B Constants |  |  |  |  | Loss Analysis 02.xls
|  | Substation Transformers |  | Primary Conductor |  | Distribution Transformers |  | Secondary Conductor
|  | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant
| 1995 | 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07
| 2001 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 2001 Modified | #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF!
| Load |  | Sub Trf Losses |  | Primary Cond Losses |  | Dist Trf Losses |  | Sec Cond Losses |  | Total Losses | Total Losses
| (MW) |  | (MW) | (%) | (MW) | (%) | (MW) | (%) | (MW) | (%) | (MW) | (%)
1995 | 4000 |  | 22.7412 | 0.5685% | 16.6095 | 0.4152% | 106.3877 | 2.66% | 6.3214 | 0.158% | 152.0598 | 3.801%
2001 | 4000 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2001 M | 4000 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1995 | 7600 |  | 37.0131 | 0.9253% | 60.0587 | 1.501% | 130.2566 | 3.256% | 23.1303 | 0.5783% | 250.4587 | 3.296%
2001 | 7600 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2001 M | 7600 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1995 | 11200 |  | 60.1434 | 1.504% | 130.3012 | 3.258% | 168.4144 | 4.21% | 50.0129 | 1.25% | 408.8719 | 3.651%
2001 | 11200 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2001 M | 11200 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Note: All % calculations are based on the total load which is shown in column 2.

## Loss Analysis 1995 (hidden)
HL&P Distribution Loss Analysis |  |  | 1995 |  | Loss Analysis 02.xls | [6 empty] | K = | 0 | K = | 0.8 | K = | 1
|  |  | PELCAR | [7 empty] | Difference |  | Tangent ? | Difference | K Formula | Difference | K Formula | Losses Based | Difference
| Input to Sub Trfs | Sub Trf Losses | Input to Dist Sys | Pri Cond Losses | Input to Dist Trfs | Dist Trf Losses | Input to Secondary | Secondary Losses | Total Losses | Tangent ? | Losses - Tangent | Total Losses | K = 0.0 | Loss - (K=0.0) | K = 0.8 | Loss - (K=0.8) | K = 1.0 | On K = 0.8 | Loss - (K=0.8)
| (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (%) | (%) | (%) | (%) | (%) | (%) | (MW) | (MW)
1 | 2400 | 19.2415 | 2380.7585 | 5.9514 | 2374.8071 | 100.482 | 2274.325 | 2.2011 | 127.8761 | 79.0922 | 48.7838 | 5.328% | 1.041% | 4.287% | 2.845% | 2.484% | 3.296% | 68.2691 | 59.607
2 | 2800 | 19.9524 | 2780.0476 | 8.1151 | 2771.9325 | 101.6834 | 2670.2491 | 3.0341 | 132.7851 | 92.2743 | 40.5108 | 4.742% | 1.214% | 3.528% | 2.879% | 1.863% | 3.296% | 80.6186 | 52.1665
3 | 3200 | 20.7726 | 3179.2274 | 10.6129 | 3168.6145 | 103.0686 | 3065.5459 | 3.999 | 138.453 | 105.4563 | 32.9967 | 4.327% | 1.388% | 2.939% | 2.914% | 1.413% | 3.296% | 93.2456 | 45.2075
4 | 3600 | 21.7022 | 3578.2978 | 13.4444 | 3564.8534 | 104.6369 | 3460.2165 | 5.0949 | 144.8784 | 118.6383 | 26.2401 | 4.024% | 1.561% | 2.463% | 2.949% | 1.076% | 3.296% | 106.1501 | 38.7284
5 | 4000 | 22.7412 | 3977.2588 | 16.6095 | 3960.6493 | 106.3877 | 3854.2617 | 6.3214 | 152.0598 | 131.8204 | 20.2394 | 3.801% | 1.734% | 2.067% | 2.983% | 0.8182% | 3.296% | 119.3321 | 32.7277
6 | 4400 | 23.8895 | 4376.1105 | 20.1079 | 4356.0027 | 108.3204 | 4247.6823 | 7.6778 | 159.9955 | 145.0024 | 14.9931 | 3.636% | 1.908% | 1.728% | 3.018% | 0.6183% | 3.296% | 132.7917 | 27.2038
7 | 4800 | 25.1472 | 4774.8528 | 23.9392 | 4750.9137 | 110.4343 | 4640.4793 | 9.1634 | 168.6841 | 158.1844 | 10.4997 | 3.514% | 2.081% | 1.433% | 3.053% | 0.4616% | 3.296% | 146.5287 | 22.1554
8 | 5200 | 26.5142 | 5173.4858 | 28.1032 | 5145.3826 | 112.729 | 5032.6536 | 10.7777 | 178.1241 | 171.3665 | 6.7576 | 3.425% | 2.255% | 1.171% | 3.087% | 0.3381% | 3.296% | 160.5433 | 17.5808
9 | 5600 | 27.9906 | 5572.0094 | 32.5997 | 5539.4098 | 115.2037 | 5424.2061 | 12.52 | 188.3139 | 184.5485 | 3.7654 | 3.363% | 2.428% | 0.9345% | 3.122% | 0.2407% | 3.296% | 174.8354 | 13.4785
10 | 6000 | 29.5764 | 5970.4236 | 37.4283 | 5932.9954 | 117.8578 | 5815.1376 | 14.3897 | 199.2521 | 197.7305 | 1.5216 | 3.321% | 2.602% | 0.7192% | 3.157% | 0.1641% | 3.296% | 189.405 | 9.8471 | Highlighted Area Represents 96% Range
11 | 6400 | 31.2715 | 6368.7285 | 42.5887 | 6326.1398 | 120.6908 | 6205.449 | 16.3862 | 210.9372 | 210.9126 | 0.024651 | 3.296% | 2.775% | 0.5207% | 3.191% | 0.1045% | 3.296% | 204.2522 | 6.685
12 | 6800 | 33.076 | 6766.924 | 48.0808 | 6718.8432 | 123.702 | 6595.1412 | 18.5089 | 223.3677 | 224.0946 | -0.72694 | 3.285% | 2.949% | 0.3362% | 3.226% | 0.05869% | 3.296% | 219.3768 | 3.9908
13 | 7200 | 34.9898 | 7165.0102 | 53.9042 | 7111.1059 | 126.8908 | 6984.2152 | 20.7571 | 236.542 | 237.2766 | -0.73466 | 3.285% | 3.122% | 0.1632% | 3.261% | 0.02449% | 3.296% | 234.779 | 1.763
14 | 7600 | 37.0131 | 7562.9869 | 60.0587 | 7502.9282 | 130.2566 | 7372.6717 | 23.1303 | 250.4587 | 250.4587 | 0 | 3.296% | 3.296% | 0% | 3.296% | 0% | 3.296% | 250.4587 | 0
15 | 8000 | 39.1456 | 7960.8544 | 66.544 | 7894.3104 | 133.7988 | 7760.5116 | 25.6279 | 265.1163 | 263.6407 | 1.4756 | 3.314% | 3.469% | -0.155% | 3.33% | -0.01625% | 3.296% | 266.4159 | -1.2996
16 | 8400 | 41.3876 | 8358.6124 | 73.3597 | 8285.2527 | 137.5168 | 8147.7359 | 28.2492 | 280.5133 | 276.8228 | 3.6905 | 3.339% | 3.642% | -0.303% | 3.365% | -0.02544% | 3.296% | 282.6506 | -2.1373
17 | 8800 | 43.7389 | 8756.2611 | 80.5057 | 8675.7554 | 141.41 | 8534.3454 | 30.9936 | 296.6482 | 290.0048 | 6.6434 | 3.371% | 3.816% | -0.4449% | 3.4% | -0.02858% | 3.296% | 299.1628 | -2.5146
18 | 9200 | 46.1996 | 9153.8004 | 87.9817 | 9065.8188 | 145.4777 | 8920.341 | 33.8606 | 313.5196 | 303.1868 | 10.3328 | 3.408% | 3.989% | -0.5815% | 3.434% | -0.02645% | 3.296% | 315.9526 | -2.433
19 | 9600 | 48.7696 | 9551.2304 | 95.7873 | 9455.4431 | 149.7195 | 9305.7236 | 36.8496 | 331.126 | 316.3689 | 14.7571 | 3.449% | 4.163% | -0.7135% | 3.469% | -0.01973% | 3.296% | 333.0199 | -1.8939
20 | 10000 | 51.449 | 9948.551 | 103.9224 | 9844.6286 | 154.1346 | 9690.494 | 39.9599 | 349.4659 | 329.5509 | 19.915 | 3.495% | 4.336% | -0.8415% | 3.504% | -0.008988% | 3.296% | 350.3646 | -0.89877
21 | 10400 | 54.2378 | 10345.7622 | 112.3865 | 10233.3757 | 158.7226 | 10074.6531 | 43.1909 | 368.5378 | 342.7329 | 25.8049 | 3.544% | 4.51% | -0.966% | 3.538% | 0.005297% | 3.296% | 367.9869 | 0.55086
22 | 10800 | 57.1359 | 10742.8641 | 121.1796 | 10621.6845 | 163.4827 | 10458.2018 | 46.5421 | 388.3403 | 355.915 | 32.4253 | 3.596% | 4.683% | -1.087% | 3.573% | 0.02272% | 3.296% | 385.8868 | 2.4536
23 | 11200 | 60.1434 | 11139.8566 | 130.3012 | 11009.5554 | 168.4144 | 10841.141 | 50.0129 | 408.8719 | 369.097 | 39.7749 | 3.651% | 4.857% | -1.206% | 3.608% | 0.04293% | 3.296% | 404.0641 | 4.8079
24 | 11600 | 63.2602 | 11536.7398 | 139.7512 | 11396.9886 | 173.5171 | 11223.4715 | 53.6027 | 430.1312 | 382.279 | 47.8522 | 3.708% | 5.03% | -1.322% | 3.642% | 0.06562% | 3.296% | 422.5189 | 7.6123
25 | 12000 | 66.4864 | 11933.5136 | 149.5292 | 11783.9844 | 178.7903 | 11605.1941 | 57.3109 | 452.1168 | 395.4611 | 56.6557 | 3.768% | 5.203% | -1.436% | 3.677% | 0.09055% | 3.296% | 441.2513 | 10.8654
26 | 12400 | 69.822 | 12330.178 | 159.635 | 12170.543 | 184.2332 | 11986.3098 | 61.1369 | 474.827 | 408.6431 | 66.1839 | 3.829% | 5.377% | -1.548% | 3.712% | 0.1175% | 3.296% | 460.2612 | 14.5658
27 | 12800 | 73.267 | 12726.733 | 170.0682 | 12556.6648 | 189.8453 | 12366.8195 | 65.0801 | 498.2606 | 421.8251 | 76.4355 | 3.893% | 5.55% | -1.658% | 3.746% | 0.1462% | 3.296% | 479.5486 | 18.712
| % Losses at Peak = | 0.5724% |  | 1.336% |  | 1.512% |  | 0.5262%
400
| Substation Transformers |  | Primary Conductor |  | Distribution Transformers |  | Secondary Conductor
| B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant
| 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07
| 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07 | 1995
| #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2001
| #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF! | 2001 Modified

## 2) Loss Analysis
|  | CenterPoint Energy Distribution Loss Factor for |  |  |  |  | 2020 | Rev 0.xls | [6 empty] | No Scaling | With Scaling | Using F1, F2 & F3 Coefficients |  | No Scaling | With Scaling
ERCOT | ERCOT |  | CNP | CNP |  | PELCAR | Primary | Total | Total |  |  | 2017 | Secondary | 2017 | 2017 | 2017 | 2017 | 2017 | Total | 2017 | Adjustment for % Losses |  | 2008 | 2008
Load (15 min) | Load (1 hr) |  | Load (15 min) | Input To Sub Trfs | Sub Trf Losses | Input to Dist Sys | Conductor Losses | Primary Losses | Primary Loss % | Input to Dist Trfs | Dist Trf Losses | Input To Secondary | Conductor Losses | Total Losses | Total Losses | Total Losses | DLF | DLF | Primary Loss % | Primary Loss % | Sec | Pri | Primary MW Losses | Sec MW Losses
|  |  |  | (MW) | (MW) | (MW) | (MW) |  |  | (MW) | (MW) | (MW) | (MW) | (MW) | (%) | (%) | Secondary | Primary
SIEL | [15 empty] | 0% |  |  |  | 0%
|  |  |  | 50 | 18.5694 | 31.4306 | 0.0011256 | 18.5706 | 37.14% | 31.4294 | 156.7244 | -125.295 | 0.0055646 | 175.3005 | 350.6% | 350.6%
|  |  |  | 135 | 18.5721 | 116.4279 | 0.015445 | 18.5876 | 13.77% | 116.4124 | 156.7294 | -40.317 | 0.00057616 | 175.3176 | 129.9% | 129.9%
|  |  |  | 500 | 18.6121 | 481.3879 | 0.26404 | 18.8761 | 3.775% | 481.1239 | 156.8167 | 324.3071 | 0.03728 | 175.7301 | 35.15% | 35.15%
1373.5772 | 5494.3087 |  | 250 | 1000 | 18.7414 | 981.2586 | 1.0971 | 19.8385 | 1.984% | 980.1615 | 157.1088 | 823.0527 | 0.24012 | 177.1874 | 17.72% | 17.72%
3296.5852 | 13186.341 | 1 | 600 | 2400 | 19.5621 | 2380.4379 | 6.4563 | 26.0185 | 1.084% | 2373.9815 | 158.9813 | 2215.0002 | 1.7391 | 186.7388 | 7.781% | 7.781% | 7.172% | 0.5227% | 1.084% | 1.084% |  |  | 26.0185 | 186.7388
3846.0161 | 15384.0645 | 2 | 700 | 2800 | 19.9207 | 2780.0793 | 8.8062 | 28.7269 | 1.026% | 2771.2731 | 159.8001 | 2611.473 | 2.4173 | 190.9443 | 6.819% | 6.819% | 6.323% | 0.5644% | 1.026% | 1.026% |  |  | 28.7269 | 190.9443
4395.447 | 17581.788 | 3 | 800 | 3200 | 20.3346 | 3179.6654 | 11.5195 | 31.8541 | 0.9954% | 3168.1459 | 160.7442 | 3007.4017 | 3.2059 | 195.8042 | 6.119% | 6.119% | 5.708% | 0.6114% | 0.9954% | 0.9954% |  |  | 31.8541 | 195.8042
4944.8779 | 19779.5114 | 4 | 900 | 3600 | 20.8035 | 3579.1965 | 14.5963 | 35.3998 | 0.9833% | 3564.6002 | 161.8133 | 3402.7868 | 4.1043 | 201.3174 | 5.592% | 5.592% | 5.25% | 0.6618% | 0.9833% | 0.9833% |  |  | 35.3998 | 201.3174
5494.3087 | 21977.2349 | 5 | 1000 | 4000 | 21.3277 | 3978.6723 | 18.0364 | 39.364 | 0.9841% | 3960.636 | 163.007 | 3797.629 | 5.112 | 207.483 | 5.187% | 5.187% | 4.902% | 0.7147% | 0.9841% | 0.9841% |  |  | 39.364 | 207.483
6043.7396 | 24174.9584 | 6 | 1100 | 4400 | 21.907 | 4378.093 | 21.8395 | 43.7465 | 0.9942% | 4356.2535 | 164.3249 | 4191.9286 | 6.2287 | 214.3 | 4.87% | 4.87% | 4.634% | 0.7694% | 0.9942% | 0.9942% |  |  | 43.7465 | 214.3
6593.1705 | 26372.6819 | 7 | 1200 | 4800 | 22.5415 | 4777.4585 | 26.0056 | 48.5471 | 1.011% | 4751.4529 | 165.7665 | 4585.6864 | 7.4538 | 221.7674 | 4.62% | 4.62% | 4.425% | 0.8254% | 1.011% | 1.011% |  |  | 48.5471 | 221.7674
7142.6014 | 28570.4054 | 8 | 1300 | 5200 | 23.2312 | 5176.7688 | 30.5344 | 53.7656 | 1.034% | 5146.2344 | 167.3316 | 4978.9028 | 8.7869 | 229.8841 | 4.421% | 4.421% | 4.263% | 0.8824% | 1.034% | 1.034% |  |  | 53.7656 | 229.8841
7692.0322 | 30768.1289 | 9 | 1400 | 5600 | 23.976 | 5576.024 | 35.426 | 59.402 | 1.061% | 5540.598 | 169.0196 | 5371.5784 | 10.2275 | 238.6491 | 4.262% | 4.262% | 4.136% | 0.9403% | 1.061% | 1.061% |  |  | 59.402 | 238.6491
8241.4631 | 32965.8524 | 10 | 1500 | 6000 | 24.776 | 5975.224 | 40.68 | 65.456 | 1.091% | 5934.544 | 170.8303 | 5763.7137 | 11.7753 | 248.0616 | 4.134% | 4.134% | 4.039% | 0.9988% | 1.091% | 1.091% |  |  | 65.456 | 248.0616
8790.894 | 35163.5759 | 11 | 1600 | 6400 | 25.6312 | 6374.3688 | 46.2964 | 71.9276 | 1.124% | 6328.0724 | 172.7631 | 6155.3093 | 13.4297 | 258.1204 | 4.033% | 4.033% | 3.965% | 1.058% | 1.124% | 1.124% |  |  | 71.9276 | 258.1204
9340.3248 | 37361.2994 | 12 | 1700 | 6800 | 26.5416 | 6773.4584 | 52.2749 | 78.8165 | 1.159% | 6721.1835 | 174.8178 | 6546.3658 | 15.1903 | 268.8246 | 3.953% | 3.953% | 3.91% | 1.117% | 1.159% | 1.159% |  |  | 78.8165 | 268.8246
9889.7557 | 39559.0229 | 13 | 1800 | 7200 | 27.5071 | 7172.4929 | 58.6155 | 86.1226 | 1.196% | 7113.8774 | 176.9938 | 6936.8836 | 17.0567 | 280.1732 | 3.891% | 3.891% | 3.872% | 1.177% | 1.196% | 1.196% |  |  | 86.1226 | 280.1732
10439.1866 | 41756.7464 | 14 | 1900 | 7600 | 28.5278 | 7571.4722 | 65.318 | 93.8458 | 1.235% | 7506.1542 | 179.2909 | 7326.8633 | 19.0284 | 292.1652 | 3.844% | 3.844% | 3.847% | 1.237% | 1.235% | 1.235% | 0 | 0 | 93.8458 | 292.1652
10988.6175 | 43954.4699 | 15 | 2000 | 8000 | 29.6037 | 7970.3963 | 72.3823 | 101.986 | 1.275% | 7898.014 | 181.7086 | 7716.3054 | 21.105 | 304.7996 | 3.81% | 3.826% | 3.833% | 1.297% | 1.275% | 1.291% | 1 | 1 | 103.282 | 306.0417
11538.0483 | 46152.1934 | 16 | 2100 | 8400 | 30.7347 | 8369.2653 | 79.8081 | 110.5429 | 1.316% | 8289.4571 | 184.2466 | 8105.2105 | 23.2861 | 318.0755 | 3.787% | 3.818% | 3.83% | 1.358% | 1.316% | 1.348% | 2 | 2 | 113.2645 | 320.6839
12087.4792 | 48349.9169 | 17 | 2200 | 8800 | 31.921 | 8768.079 | 87.5954 | 119.5164 | 1.358% | 8680.4836 | 186.9044 | 8493.5792 | 25.5711 | 331.9918 | 3.773% | 3.819% | 3.835% | 1.419% | 1.358% | 1.407% | 3 | 3 | 123.7932 | 336.0908
12636.9101 | 50547.6404 | 18 | 2300 | 9200 | 33.1624 | 9166.8376 | 95.744 | 128.9064 | 1.401% | 9071.0936 | 189.6817 | 8881.412 | 27.9596 | 346.5476 | 3.767% | 3.829% | 3.847% | 1.48% | 1.401% | 1.466% | 4 | 4 | 134.868 | 352.2613
13186.341 | 52745.3639 | 19 | 2400 | 9600 | 34.459 | 9565.541 | 104.2537 | 138.7127 | 1.445% | 9461.2873 | 192.578 | 9268.7093 | 30.4513 | 361.742 | 3.768% | 3.846% | 3.866% | 1.541% | 1.445% | 1.526% | 5 | 5 | 146.4887 | 369.1946
13735.7718 | 54943.0874 | 20 | 2500 | 10000 | 35.8107 | 9964.1893 | 113.1244 | 148.9351 | 1.489% | 9851.0649 | 195.593 | 9655.4719 | 33.0456 | 377.5738 | 3.776% | 3.869% | 3.891% | 1.602% | 1.489% | 1.587% | 6 | 6 | 158.6551 | 386.8896
14285.2027 | 57140.8108 | 21 | 2600 | 10400 | 37.2176 | 10362.7824 | 122.356 | 159.5736 | 1.534% | 10240.4264 | 198.7263 | 10041.7001 | 35.7422 | 394.0422 | 3.789% | 3.898% | 3.921% | 1.663% | 1.534% | 1.648% | 7 | 7 | 171.3672 | 405.3453
14834.6336 | 59338.5343 | 22 | 2700 | 10800 | 38.6797 | 10761.3203 | 131.9482 | 170.6279 | 1.58% | 10629.3721 | 201.9775 | 10427.3945 | 38.5406 | 411.1461 | 3.807% | 3.931% | 3.955% | 1.725% | 1.58% | 1.709% | 8 | 8 | 184.6247 | 424.5608
15384.0645 | 61536.2578 | 23 | 2800 | 11200 | 40.197 | 11159.803 | 141.901 | 182.098 | 1.626% | 11017.902 | 205.3462 | 10812.5558 | 41.4404 | 428.8846 | 3.829% | 3.969% | 3.994% | 1.786% | 1.626% | 1.772% | 9 | 9 | 198.4276 | 444.5352
15933.4953 | 63733.9813 | 24 | 2900 | 11600 | 41.7694 | 11558.2306 | 152.2142 | 193.9836 | 1.672% | 11406.0164 | 208.8321 | 11197.1843 | 44.4411 | 447.2568 | 3.856% | 4.011% | 4.035% | 1.848% | 1.672% | 1.834% | 10 | 10 | 212.7756 | 465.2673
16482.9262 | 65931.7048 | 25 | 3000 | 12000 | 43.397 | 11956.603 | 162.8876 | 206.2846 | 1.719% | 11793.7154 | 212.4347 | 11581.2807 | 47.5423 | 466.2617 | 3.886% | 4.056% | 4.081% | 1.909% | 1.719% | 1.897% | 11 | 11 | 227.6686 | 486.7564
17032.3571 | 68129.4283 | 26 | 3100 | 12400 | 45.0798 | 12354.9202 | 173.9211 | 219.0009 | 1.766% | 12180.9991 | 216.1536 | 11964.8454 | 50.7436 | 485.8982 | 3.919% | 4.105% | 4.129% | 1.971% | 1.766% | 1.961% | 12 | 12 | 243.1065 | 509.0014
17581.788 | 70327.1518 | 27 | 3200 | 12800 | 46.8178 | 12753.1822 | 185.3146 | 232.1324 | 1.814% | 12567.8676 | 219.9885 | 12347.8791 | 54.0446 | 506.1655 | 3.954% | 4.156% | 4.179% | 2.033% | 1.814% | 2.024% | 13 | 13 | 259.0892 | 532.0013
18131.2188 | 72524.8753 | 28 | 3300 | 13200 | 48.6109 | 13151.3891 | 197.0678 | 245.6787 | 1.861% | 12954.3213 | 223.9391 | 12730.3822 | 57.4447 | 527.0625 | 3.993% | 4.21% | 4.233% | 2.095% | 1.861% | 2.088% | 14 | 14 | 275.6163 | 555.7551
18680.6497 | 74722.5988 | 29 | 3400 | 13600 | 50.4592 | 13549.5408 | 209.1807 | 259.6399 | 1.909% | 13340.3601 | 228.0048 | 13112.3553 | 60.9437 | 548.5884 | 4.034% | 4.267% | 4.288% | 2.157% | 1.909% | 2.152% | 15 | 15 | 292.6879 | 580.262
19230.0806 | 76920.3223 | 30 | 3500 | 14000 | 52.3627 | 13947.6373 | 221.653 | 274.0158 | 1.957% | 13725.9842 | 232.1853 | 13493.7989 | 64.541 | 570.7421 | 4.077% | 4.325% | 4.345% | 2.219% | 1.957% | 2.216% | 16 | 16 | 310.3038 | 605.521
19779.5114 | 79118.0458 | 31 | 3600 | 14400 | 54.3214 | 14345.6786 | 234.4847 | 288.8061 | 2.006% | 14111.1939 | 236.4803 | 13874.7136 | 68.2363 | 593.5227 | 4.122% | 4.386% | 4.405% | 2.281% | 2.006% | 2.281% | 17 | 17 | 328.4637 | 631.5311
20328.9423 | 81315.7693 | 32 | 3700 | 14800 | 56.3352 | 14743.6648 | 247.6756 | 304.0109 | 2.054% | 14495.9891 | 240.8893 | 14255.0999 | 72.0291 | 616.9292 | 4.168% | 4.448% | 4.465% | 2.343% | 2.054% | 2.346% | 18 | 18 | 347.1677 | 658.2913
20878.3732 | 83513.4928 | 33 | 3800 | 15200 | 58.4042 | 15141.5958 | 261.2256 | 319.6298 | 2.103% | 14880.3702 | 245.412 | 14634.9582 | 75.919 | 640.9607 | 4.217% | 4.512% | 4.528% | 2.405% | 2.103% | 2.411% | 19 | 19 | 366.4154 | 685.8007
21427.8041 | 85711.2163 | 34 | 3900 | 15600 | 60.5284 | 15539.4716 | 275.1344 | 335.6628 | 2.152% | 15264.3372 | 250.048 | 15014.2892 | 79.9055 | 665.6163 | 4.267% | 4.577% | 4.592% | 2.467% | 2.152% | 2.476% | 20 | 20 | 386.2068 | 714.0584
21977.2349 | 87908.9398 | 35 | 4000 | 16000 | 62.7078 | 15937.2922 | 289.402 | 352.1097 | 2.201% | 15647.8903 | 254.7969 | 15393.0934 | 83.9883 | 690.8949 | 4.318% | 4.644% | 4.657% | 2.529% | 2.201% | 2.541% | 21 | 21 | 406.5417 | 743.0633
22938.739 | 91754.9559 |  | 4175 | 16700 | 66.6544 | 16633.3456 | 315.233 | 381.8873 | 2.287% | 16318.1127 | 263.378 | 16054.7347 | 91.3637 | 736.629 | 4.411% | 4.753% | 4.774% | 2.638% | 2.287% | 2.643% | 22 | 22
[21 empty] | 23 | 23
10740 | 42960 |  | 1954.75 | 7819 |  | 7789.613
15 min | ERCOT |  | 15 min | CNP | [12 empty] | Secondary | Primary | CNP
10740 | 42960 | AAL | 1954.75 | 7819 | 29.387 | 7789.613 | 69.136 | 98.5229 | 1.26% | 7720.4771 | 183.3065 | 7537.1706 | 20.1365 | 301.9659 | 3.862% |  | 3.838% | 1.27% | At ERCOT AAL
18686 | 74744 | Peak | 3917.93 | 15671.72 | 63.7203 | 15607.9997 | 277.5664 | 341.2867 | 2.178% | 15330.4333 | 251.9373 | 15078.496 | 80.5904 | 673.8144 | 4.3% |  | 4.289% | 2.157% | At ERCOT Peak
| 1.7399 |  |  | 2.0043
AAL for CNP (7,790 MW) is measured at the Dist Fdr Bkr (PELCAR, Column G) so this value is increased 29 MW (Cell F50 ) for the high side of the sub trfs
Peak for CNP (15,608 MW) is measured at the Dist Fdr Bkr (PELCAR, Column G) so this value is increased 63 MW (Cell F51) for the high side of the sub trfs
CNP peak is proportionately higher than CNP AAL as compared to ERCOT peak vs ERCOT AAL, so % Losses above AAL are scaled proportionately ---> | [14 empty] | Scaling for % Losses |  |  | 2019
(When ERCOT is at peak, CNP is 5 intervals below peak, so % losses at ERCOT peak are scaled up to match % losses at CNP peak.) | [14 empty] | Secondary | Primary |  | For Secondary Distribution Customers "D"
|  |  |  | Substation Transformers |  | Primary Conductor |  |  |  | Distribution Transformers |  | Secondary Conductor |  |  | 0.295% | 0.243% |  | For Primary Distribution Customers "E"
|  |  |  | B Constant | A Constant | B Constant | A Constant |  |  | B Constant | A Constant | B Constant | A Constant |  |  |  | Primary Constants
|  | 2019 Values ----> |  | 18.008 | 1.8612e-07 | 0 | 1.1394e-06 |  |  | 159.986 | 3.9124e-07 | 0 | 3.5446e-07 | <----2019 Values
|  | 2018 Values ----> |  | 18.569 | 1.7242e-07 | 0 | 1.1394e-06 |  |  | 156.724 | 4.0053e-07 | 0 | 3.5446e-07 | <----2018 Values |  |  | F1 = | 0.01225 | right
|  | 2017 Values ----> |  | 18.268 | 1.7762e-07 | 0 | 1.1394e-06 |  |  | 152.212 | 4.0973e-07 | 0 | 3.5446e-07 | <--- 2017 Values |  |  | F2 = | 1e-06 | middle
|  | 2016 Values ----> |  | 20.6354 | 1.8059e-07 | 0 | 1.1394e-06 |  |  | 149.175 | 4.2041e-07 | 0 | 3.5446e-07 | <--- 2016 Values |  |  | F3 = | 0.00045 | left
|  | 2015 Values ----> |  | 20.867 | 1.7797e-07 | 0 | 1.1394e-06 |  |  | 145.39 | 4.3561e-07 | 0 | 3.5446e-07 | <--- 2015 Values
|  | 2014 Values ----> |  | 19.863 | 1.893e-07 | 0 | 1.1394e-06 |  |  | 142.346 | 4.4856e-07 | 0 | 3.5446e-07 | <--- 2014 Values
|  | 2013 Values ----> |  | 19.473 | 1.9548e-07 | 0 | 1.1394e-06 |  |  | 137.751 | 4.7391e-07 | 0 | 3.5446e-07 | <--- 2013 Values |  |  |  | Secondary Constants
|  | 2012 Values ----> |  | 21.1118 | 1.8286e-07 | 0 | 1.1394e-06 |  |  | 133.986 | 5.0407e-07 | 0 | 3.5446e-07 | <--- 2012 Values
|  | 2009 Values ----> |  | 20.312 | 1.9194e-07 | 0 | 1.1394e-06 |  |  | 130.794 | 5.041e-07 | 0 | 3.5446e-07 | <--- 2009 Values
|  | 2008 Values ----> |  | 18.586 | 2.13e-07 | 0 | 1.1394e-06 |  |  | 120.235 | 5.139e-07 | 0 | 3.5446e-07 | <--- 2008 Values |  |  | F1 = | 0.0177 | right
|  | 2007 Values ----> |  | 18.586 | 2.13e-07 | 0 | 1.1394e-06 |  |  | 120.235 | 5.139e-07 | 0 | 3.5446e-07 | <--- 2007 Values |  |  | F2 = | 0.00048 | middle
[17 empty] | F3 = | 0.0202 | left
|  |  |  | 17.273 | 3.4176e-07 | 0 | 1.05e-06 | <--- 1995 |  | 97.167 | 5.878e-07 | 0 | 4.2553e-07 | <--- 1995
|  |  |  | 19.73 | 2.9981e-07 | 0 | 1.1116e-06 | <--- 2001 |  | 115.01 | 5.6399e-07 | 0 | 3.5446e-07 | <--- 2001
|  |  |  | 20.2955 | 2.9981e-07 | 0 | 1.1116e-06 | <--- 2004/2006 |  | 133.2966 | 5.6399e-07 | 0 | 3.5446e-07 | <--- 2004/2006
|  |  |  | 2.866% increase in Sub Trf nameplate MVA from 2001 to 2004 | [5 empty] | 15.9% 1ncrease in distribution trf nameplate KVA from 2001 to 2004
|  |  | 2007 Start Values ----> | 18.586 | 2.13e-07 | 0 | 1.1116e-06 |  |  | 120.235 | 5.139e-07 | 0 | 3.5446e-07 | <---2007 Start Value
|  |  |  | New values as per updated |  | Add 2.5 % to 2006 values due |  |  |  | New values as per updated
|  |  | 2007 Adjustments ----> | substation trf review. |  | to increased loading on circuits |  |  |  | distribution trf review.
|  |  |  | Decrease from 2006 values. |  | as per revised Design Criteria |  |  |  | Decrease from 2006 values. |  | No change to 2006 values.
[11 empty] | AAL for ERCOT (15 mins) = 10,740 |  |  | DLF = F1 * (SIEL/AAL) + F2 + F3 / (SIEL/AAL)
(See graphs below)
Primary Constants
F1 = | 0.01225 | right
F2 = | 1e-06 | middle
F3 = | 0.00045 | left
Secondary Constants
F1 = | 0.0177 | right
F2 = | 0.00048 | middle
F3 = | 0.0202 | left

## 3) Loss Equations
System Loss Equations For CenterPoint Energy for |  |  |  |  | 2020 | DLF | Color Key
INPUT - Must be changed every year
| Losses = | AX2 + B | [5 empty] | Formula - Don’t touch
A = Constant
B = Constant
X = Input to System (MW)
Substation Transformers
Calculations/Formulas
78.829 | = | A * (TRF name plate*TRF name plate) + (No load losses+1%)
| A = | 1.8612e-07
| B = | 18.008
Variables
| 2019 | for use in | 2020
Total No Load Losses for Substation Transformers [MW]: |  |  |  | 18.008
Total Load Losses at Trf base name plate rating [MW]: |  |  |  | 60.821
|  |  | Total Losses [MW]: | 78.829
Trf base name plate rating [MVA]: |  |  |  | 18077
Distribution Transformers
Calculations/Formulas
251.932 | = | A * (Distribution Input*Distribution Input) + No load losses
| A = | 3.9124e-07
| B = | 159.986
Variables
| 2019 | for use in | 2020
Total No-Load Loss Average For Distribution Transformer[MW]: |  |  |  | 159.986
Total Load Losses at input to Distribution Transformers [MW]: |  |  |  | 91.946
|  |  | Total Losses [MW]: | 251.932
Distribution Input [MW]: |  |  |  | 15330
Conductors
Primary Conductor
| A = | 1.1394e-06
| B = | 0
Secondary Conductor
| A = | 3.5446e-07
| B = | 0

## Loss Analysis 2001 Mod (hidden)
HL&P Distribution Loss Analysis |  |  | 2001 Modified |  | Loss Analysis 02.xls | [6 empty] | K = | 0 | K = | 0.8 | K = | 1
|  |  | PELCAR | [7 empty] | Difference |  | Tangent ? | Difference | K Formula | Difference | K Formula | Losses Based | Difference
| Input to Sub Trfs | Sub Trf Losses | Input to Dist Sys | Pri Cond Losses | Input to Dist Trfs | Dist Trf Losses | Input to Secondary | Secondary Losses | Total Losses | Tangent ? | Losses - Tangent | Total Losses | K = 0.0 | Loss - (K=0.0) | K = 0.8 | Loss - (K=0.8) | K = 1.0 | On K = 0.8 | Loss - (K=0.8)
| (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (%) | (%) | (%) | (%) | (%) | (%) | (MW) | (MW)
1 | 2400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2 | 2800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3 | 3200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
4 | 3600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
5 | 4000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
6 | 4400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
7 | 4800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
8 | 5200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
9 | 5600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
10 | 6000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
11 | 6400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
12 | 6800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
13 | 7200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
14 | 7600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
15 | 8000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
16 | 8400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
17 | 8800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
18 | 9200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
19 | 9600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
20 | 10000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
21 | 10400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
22 | 10800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
23 | 11200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
24 | 11600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
25 | 12000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
26 | 12400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
27 | 12800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| % Losses at Peak = | #REF! |  | #REF! |  | #REF! |  | #REF!
400
| Substation Transformers |  | Primary Conductor |  | Distribution Transformers |  | Secondary Conductor
| B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant
| #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF!
| 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07 | 1995
| #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2001
| #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF! | 2001 Modified