## Slide 1
2020 Long-Term Load Forecast
Sarah Parody
Load Forecasting & Analysis
SAWG
December 13, 2019

## Slide 2: Agenda
Load Forecasting Framework
Growth Driver
Normal Weather (P50) Forecast
ERCOT P50 Forecast

## Slide 3: Agenda
Assumptions and Challenges
Active Models
Weather Zone P50 and P90 Forecasts
Questions

## Slide 4
Load Forecasting Framework

## Slide 5: Weather Zones
2 or 3 Weather Stations in each Weather Zone

## Slide 6: Load Models
Unique Model for
  Each Weather Zone
    Each Temperature Group
      Hot
      Medium
      Cold

## Slide 7: Load Models
Unique Model for
  Each Weather Zone
    Each Temperature Group
      Hot
      Medium
      Cold
Temperature
South Load vs. Temperature
MW

## Slide 8: Temperature Groups
MW
MW
Temperature
South March
South Hot
South Medium Cold
Temperature

## Slide 9: Months vs. Temperature Groups
MW
Temperature
South March

## Slide 10: Months vs. Temperature Groups
MW
Temperature
South March
Temperature
MW
South Hot

## Slide 11: Input Data
Hourly Models
From January 2014 through August 2019
  Recent Snapshot
    Appliance Stock
    Energy Efficiency
    Demand Response
    Price Responsive Load

## Slide 12: Input Data
Weather
Calendar
Actual Load

## Slide 13: Input Data
Weather
  Temperature, Temperature Squared, and Temperature Cubed
  Cooling Degree Days and Heating Degree Days
  Cloud Cover
  Wind Speed
  Dew Point

## Slide 14: Input Data
Calendar
  Month
  Day of the Week
  Holidays
  Hour
  Interact Hour with Day of the Week

## Slide 15: Input Data
Variable Interactions
  Interact a Weather Variable with a Calendar Variable
    Temperature with Hour
    Dew Point with Hour
  Interact multiple Weather Variables with a Calendar Variable
    Temperature with Dew Point and Hour

## Slide 16
Growth Driver

## Slide 17: Premise Forecast
Unique Model for
  Each Weather Zone
    Each Premise Class
      Residential
      Commercial
      Industrial
Monthly Models

## Slide 18: Input Data
From January 2014 through August 2019
Economic Measures
  Population
  Non-Farm Employment
  Housing Stock
  Error Correction Term

## Slide 19: Challenges
Chart: Far West Historical Premise Counts
Premise Counts increased significantly via opt-in

## Slide 20: Challenges
Chart: West Historical Premise Counts
Premise Counts increased significantly via opt-in

## Slide 21: Growth Driver for Far West and West
Economic Measures from Moody’s Base Scenario
  Population
  Non-Farm Employment
  Housing Stock

## Slide 22
Normal Weather (P50) Forecast

## Slide 23: Normal Weather (P50) Forecast
Coast 2020 Summer Forecasts
Year | Month | Day | Hour | Rank | Forecast based on 2004’s Weather
2020 | 8 | 22 | 18 | 1 | 21,257
2020 | 8 | 22 | 17 | 2 | 21,166
2020 | 8 | 22 | 16 | 3 | 21,083
2020 | 8 | 21 | 18 | 4 | 20,996
2020 | 8 | 21 | 17 | 5 | 20,834
Rank | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | P50
1 | 21,257 | 20,994 | 20,757 | 20,752 | 21,015 | 20,748 | 21,295 | 21,047 | 21,857 | 21,799 | 21,132 | 20,842 | 21,582 | 21,349 | 20,738 | 21,144
2 | 21,211 | 20,840 | 20,099 | 20,542 | 20,981 | 20,368 | 21,162 | 20,950 | 21,830 | 20,910 | 20,979 | 20,839 | 21,558 | 21,064 | 20,689 | 20,935
3 | 21,191 | 20,763 | 20,095 | 20,422 | 20,769 | 20,330 | 20,938 | 20,851 | 21,631 | 20,904 | 20,926 | 20,746 | 21,353 | 20,998 | 20,542 | 20,831
4 | 21,059 | 20,740 | 20,088 | 20,294 | 20,726 | 20,305 | 20,934 | 20,814 | 21,617 | 20,825 | 20,926 | 20,718 | 21,249 | 20,977 | 20,470 | 20,783
5 | 20,923 | 20,446 | 19,976 | 20,221 | 20,708 | 20,144 | 20,844 | 20,797 | 21,568 | 20,804 | 20,897 | 20,677 | 21,211 | 20,968 | 20,462 | 20,710

## Slide 24: Normal Weather (P50) Forecast
Coast 2020 Summer Forecasts
Year | Month | Day | Hour | Rank | Forecast based on 2004’s Weather
2020 | 8 | 22 | 18 | 1 | 21,257
2020 | 8 | 22 | 17 | 2 | 21,166
2020 | 8 | 22 | 16 | 3 | 21,083
2020 | 8 | 21 | 18 | 4 | 20,996
2020 | 8 | 21 | 17 | 5 | 20,834
Rank | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | P50
1 | 21,257 | 20,994 | 20,757 | 20,752 | 21,015 | 20,748 | 21,295 | 21,047 | 21,857 | 21,799 | 21,132 | 20,842 | 21,582 | 21,349 | 20,738 | 21,144
2 | 21,211 | 20,840 | 20,099 | 20,542 | 20,981 | 20,368 | 21,162 | 20,950 | 21,830 | 20,910 | 20,979 | 20,839 | 21,558 | 21,064 | 20,689 | 20,935
3 | 21,191 | 20,763 | 20,095 | 20,422 | 20,769 | 20,330 | 20,938 | 20,851 | 21,631 | 20,904 | 20,926 | 20,746 | 21,353 | 20,998 | 20,542 | 20,831
4 | 21,059 | 20,740 | 20,088 | 20,294 | 20,726 | 20,305 | 20,934 | 20,814 | 21,617 | 20,825 | 20,926 | 20,718 | 21,249 | 20,977 | 20,470 | 20,783
5 | 20,923 | 20,446 | 19,976 | 20,221 | 20,708 | 20,144 | 20,844 | 20,797 | 21,568 | 20,804 | 20,897 | 20,677 | 21,211 | 20,968 | 20,462 | 20,710
Sort from high to low

## Slide 25: Normal Weather (P50) Forecast
Coast 2020 Summer Forecasts
Year | Month | Day | Hour | Rank | Forecast based on 2004’s Weather
2020 | 8 | 22 | 18 | 1 | 21,257
2020 | 8 | 22 | 17 | 2 | 21,166
2020 | 8 | 22 | 16 | 3 | 21,083
2020 | 8 | 21 | 18 | 4 | 20,996
2020 | 8 | 21 | 17 | 5 | 20,834
Rank | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | P50
1 | 21,257 | 20,994 | 20,757 | 20,752 | 21,015 | 20,748 | 21,295 | 21,047 | 21,857 | 21,799 | 21,132 | 20,842 | 21,582 | 21,349 | 20,738 | 21,144
2 | 21,211 | 20,840 | 20,099 | 20,542 | 20,981 | 20,368 | 21,162 | 20,950 | 21,830 | 20,910 | 20,979 | 20,839 | 21,558 | 21,064 | 20,689 | 20,935
3 | 21,191 | 20,763 | 20,095 | 20,422 | 20,769 | 20,330 | 20,938 | 20,851 | 21,631 | 20,904 | 20,926 | 20,746 | 21,353 | 20,998 | 20,542 | 20,831
4 | 21,059 | 20,740 | 20,088 | 20,294 | 20,726 | 20,305 | 20,934 | 20,814 | 21,617 | 20,825 | 20,926 | 20,718 | 21,249 | 20,977 | 20,470 | 20,783
5 | 20,923 | 20,446 | 19,976 | 20,221 | 20,708 | 20,144 | 20,844 | 20,797 | 21,568 | 20,804 | 20,897 | 20,677 | 21,211 | 20,968 | 20,462 | 20,710

## Slide 26: Normal Weather (P50) Forecast
Coast 2020 Summer Forecasts
Year | Month | Day | Hour | Rank | Forecast based on 2004’s Weather
2020 | 8 | 22 | 18 | 1 | 21,257
2020 | 8 | 22 | 17 | 2 | 21,166
2020 | 8 | 22 | 16 | 3 | 21,083
2020 | 8 | 21 | 18 | 4 | 20,996
2020 | 8 | 21 | 17 | 5 | 20,834
Rank | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | P50
1 | 21,257 | 21,208 | 21,081 | 21,499 | 21,099 | 21,858 | 21,485 | 22,220 | 22,656 | 21,458 | 21,172 | 22,031 | 21,660 | 21,074 | 21,290 | 21,536
2 | 21,166 | 20,502 | 20,895 | 21,413 | 20,756 | 21,384 | 21,266 | 22,151 | 21,250 | 21,244 | 21,132 | 21,947 | 21,406 | 21,025 | 21,257 | 21,253
3 | 21,083 | 20,421 | 20,883 | 21,358 | 20,716 | 21,277 | 21,254 | 22,128 | 21,236 | 21,211 | 21,099 | 21,589 | 21,356 | 20,902 | 21,153 | 21,178
4 | 20,996 | 20,404 | 20,603 | 21,225 | 20,641 | 21,250 | 21,170 | 22,096 | 21,152 | 21,210 | 21,001 | 21,555 | 21,348 | 20,841 | 21,131 | 21,108
5 | 20,834 | 20,382 | 20,495 | 21,131 | 20,591 | 21,156 | 21,169 | 22,040 | 21,119 | 21,188 | 20,972 | 21,545 | 21,299 | 20,792 | 21,062 | 21,052

## Slide 27: Normal Weather (P50) Forecast
Coast 2020 Summer Forecasts
Rank | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | P50
1 | 21,257 | 21,208 | 21,081 | 21,499 | 21,099 | 21,858 | 21,485 | 22,220 | 22,656 | 21,458 | 21,172 | 22,031 | 21,660 | 21,074 | 21,290 | 21,536
2 | 21,166 | 20,502 | 20,895 | 21,413 | 20,756 | 21,384 | 21,266 | 22,151 | 21,250 | 21,244 | 21,132 | 21,947 | 21,406 | 21,025 | 21,257 | 21,253
3 | 21,083 | 20,421 | 20,883 | 21,358 | 20,716 | 21,277 | 21,254 | 22,128 | 21,236 | 21,211 | 21,099 | 21,589 | 21,356 | 20,902 | 21,153 | 21,178
4 | 20,996 | 20,404 | 20,603 | 21,225 | 20,641 | 21,250 | 21,170 | 22,096 | 21,152 | 21,210 | 21,001 | 21,555 | 21,348 | 20,841 | 21,131 | 21,108
5 | 20,834 | 20,382 | 20,495 | 21,131 | 20,591 | 21,156 | 21,169 | 22,040 | 21,119 | 21,188 | 20,972 | 21,545 | 21,299 | 20,792 | 21,062 | 21,052

## Slide 28: Normal Weather (P50) Forecast
Chart: Coast 2020 Summer Peak Forecasts
| 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018
 | 21257.3872 | 21208.0153 | 21080.7538 | 21499.2553 | 21098.5938 | 21857.6111 | 21484.7698 | 22219.7904 | 22656.0454 | 21457.6694 | 21171.7986 | 22030.5948 | 21659.7427 | 21074.4763 | 21289.8129

## Slide 29: Normal Weather (P50) Forecast
Coast 2020 Summer Forecasts
Rank | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | P50
1 | 21,257 | 21,208 | 21,081 | 21,499 | 21,099 | 21,858 | 21,485 | 22,220 | 22,656 | 21,458 | 21,172 | 22,031 | 21,660 | 21,074 | 21,290 | 21,536
2 | 21,166 | 20,502 | 20,895 | 21,413 | 20,756 | 21,384 | 21,266 | 22,151 | 21,250 | 21,244 | 21,132 | 21,947 | 21,406 | 21,025 | 21,257 | 21,253
3 | 21,083 | 20,421 | 20,883 | 21,358 | 20,716 | 21,277 | 21,254 | 22,128 | 21,236 | 21,211 | 21,099 | 21,589 | 21,356 | 20,902 | 21,153 | 21,178
4 | 20,996 | 20,404 | 20,603 | 21,225 | 20,641 | 21,250 | 21,170 | 22,096 | 21,152 | 21,210 | 21,001 | 21,555 | 21,348 | 20,841 | 21,131 | 21,108
5 | 20,834 | 20,382 | 20,495 | 21,131 | 20,591 | 21,156 | 21,169 | 22,040 | 21,119 | 21,188 | 20,972 | 21,545 | 21,299 | 20,792 | 21,062 | 21,052

## Slide 30: Normal Weather (P50) Forecast
Coast 2020 Summer Forecasts
Rank | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | P50
1 | 21,257 | 21,208 | 21,081 | 21,499 | 21,099 | 21,858 | 21,485 | 22,220 | 22,656 | 21,458 | 21,172 | 22,031 | 21,660 | 21,074 | 21,290 | 21,536
2 | 21,166 | 20,502 | 20,895 | 21,413 | 20,756 | 21,384 | 21,266 | 22,151 | 21,250 | 21,244 | 21,132 | 21,947 | 21,406 | 21,025 | 21,257 | 21,253
3 | 21,083 | 20,421 | 20,883 | 21,358 | 20,716 | 21,277 | 21,254 | 22,128 | 21,236 | 21,211 | 21,099 | 21,589 | 21,356 | 20,902 | 21,153 | 21,178
4 | 20,996 | 20,404 | 20,603 | 21,225 | 20,641 | 21,250 | 21,170 | 22,096 | 21,152 | 21,210 | 21,001 | 21,555 | 21,348 | 20,841 | 21,131 | 21,108
5 | 20,834 | 20,382 | 20,495 | 21,131 | 20,591 | 21,156 | 21,169 | 22,040 | 21,119 | 21,188 | 20,972 | 21,545 | 21,299 | 20,792 | 21,062 | 21,052

## Slide 31: Normal Weather (P50) Forecast
Coast 2020 Summer Forecasts
Rank | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | P50
1 | 21,257 | 21,208 | 21,081 | 21,499 | 21,099 | 21,858 | 21,485 | 22,220 | 22,656 | 21,458 | 21,172 | 22,031 | 21,660 | 21,074 | 21,290 | 21,536
2 | 21,166 | 20,502 | 20,895 | 21,413 | 20,756 | 21,384 | 21,266 | 22,151 | 21,250 | 21,244 | 21,132 | 21,947 | 21,406 | 21,025 | 21,257 | 21,253
3 | 21,083 | 20,421 | 20,883 | 21,358 | 20,716 | 21,277 | 21,254 | 22,128 | 21,236 | 21,211 | 21,099 | 21,589 | 21,356 | 20,902 | 21,153 | 21,178
4 | 20,996 | 20,404 | 20,603 | 21,225 | 20,641 | 21,250 | 21,170 | 22,096 | 21,152 | 21,210 | 21,001 | 21,555 | 21,348 | 20,841 | 21,131 | 21,108
5 | 20,834 | 20,382 | 20,495 | 21,131 | 20,591 | 21,156 | 21,169 | 22,040 | 21,119 | 21,188 | 20,972 | 21,545 | 21,299 | 20,792 | 21,062 | 21,052

## Slide 32: Normal Weather (P50) Forecast
Chart: Coast 2020 Summer Peak Forecasts
| 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | Highest | Lowest | P50
 | 21257.3872 | 21208.0153 | 21080.7538 | 21499.2553 | 21098.5938 | 21857.6111 | 21484.7698 | 22219.7904 | 22656.0454 | 21457.6694 | 21171.7986 | 22030.5948 | 21659.7427 | 21074.4763 | 21289.8129 | 22656.0454 | 21074.4763 | 21536.4211

## Slide 33: Normal Weather (P50) Forecast
For every weather zone
For every forecasted year (2020-2029)

## Slide 34: Normal Weather (P50) Forecast
Rank | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | P50
1 | 21,257 | 21,208 | 21,081 | 21,499 | 21,099 | 21,858 | 21,485 | 22,220 | 22,656 | 21,458 | 21,172 | 22,031 | 21,660 | 21,074 | 21,290 | 21,536
2 | 21,166 | 20,502 | 20,895 | 21,413 | 20,756 | 21,384 | 21,266 | 22,151 | 21,250 | 21,244 | 21,132 | 21,947 | 21,406 | 21,025 | 21,257 | 21,253
3 | 21,083 | 20,421 | 20,883 | 21,358 | 20,716 | 21,277 | 21,254 | 22,128 | 21,236 | 21,211 | 21,099 | 21,589 | 21,356 | 20,902 | 21,153 | 21,178
4 | 20,996 | 20,404 | 20,603 | 21,225 | 20,641 | 21,250 | 21,170 | 22,096 | 21,152 | 21,210 | 21,001 | 21,555 | 21,348 | 20,841 | 21,131 | 21,108
5 | 20,834 | 20,382 | 20,495 | 21,131 | 20,591 | 21,156 | 21,170 | 22,040 | 21,119 | 21,188 | 20,972 | 21,545 | 21,299 | 20,792 | 21,062 | 21,052
Forecasted values are
  Ranked from high to low
  Averaged by Rank
Coast 2020 Summer Forecasts

## Slide 35
ERCOT P50 Forecast

## Slide 36: ERCOT P50 Forecast
Historical Year | Month | Day | Hour | Rank | Actual Load
2008 | 8 | 1 | 17 | 1 | 17,623
2008 | 8 | 1 | 16 | 2 | 17,478
2008 | 8 | 1 | 18 | 3 | 17,463
2008 | 8 | 8 | 17 | 4 | 17,222
2008 | 8 | 8 | 18 | 5 | 17,184
Coast 2008 Summer Actual Load

## Slide 37: ERCOT P50 Forecast
Historical Year | Month | Day | Hour | Rank | Actual Load
2008 | 8 | 1 | 17 | 1 | 17,623
2008 | 8 | 1 | 16 | 2 | 17,478
2008 | 8 | 1 | 18 | 3 | 17,463
2008 | 8 | 8 | 17 | 4 | 17,222
2008 | 8 | 8 | 18 | 5 | 17,184
Coast 2008 Summer Actual Load
Sort from high to low

## Slide 38: ERCOT P50 Forecast
Historical Year | Month | Day | Hour | Rank | Actual Load
2008 | 8 | 1 | 17 | 1 | 17,623
2008 | 8 | 1 | 16 | 2 | 17,478
2008 | 8 | 1 | 18 | 3 | 17,463
2008 | 8 | 8 | 17 | 4 | 17,222
2008 | 8 | 8 | 18 | 5 | 17,184
Coast 2008 Summer Actual Load
Ranks

## Slide 39: ERCOT P50 Forecast
Historical Year | Month | Day | Hour | Rank | Actual Load
2008 | 8 | 1 | 17 | 1 | 17,623
2008 | 8 | 1 | 16 | 2 | 17,478
2008 | 8 | 1 | 18 | 3 | 17,463
2008 | 8 | 8 | 17 | 4 | 17,222
2008 | 8 | 8 | 18 | 5 | 17,184
Coast 2008 Summer Actual Load
Ranks
and Coast 2020 Forecast
P50 Forecast | Forecast Year
21,536 | 2020
21,253 | 2020
21,178 | 2020
21,108 | 2020
21,052 | 2020

## Slide 40: ERCOT P50 Forecast
Forecast Year | Month | Day | Hour | COAST | EAST | FWEST | NCENT | NORTH | SCENT | SOUTH | WEST | ERCOT
2020 | 8 | 4 | 17 | 20,798 | 2,648 | 4,963 | 26,012 | 1,498 | 12,908 | 5,763 | 2,107 | 76,696
2020 | 8 | 1 | 17 | 21,536 | 2,742 | 4,932 | 25,197 | 1,455 | 12,143 | 5,711 | 1,927 | 75,643
2020 | 8 | 4 | 18 | 20,572 | 2,672 | 4,944 | 25,607 | 1,470 | 12,637 | 5,652 | 2,041 | 75,597
2020 | 8 | 4 | 16 | 20,712 | 2,664 | 4,920 | 25,525 | 1,465 | 12,465 | 5,728 | 2,037 | 75,515
2020 | 8 | 7 | 17 | 20,982 | 2,656 | 4,836 | 25,097 | 1,404 | 12,350 | 5,891 | 1,975 | 75,192
Historical Year | Month | Day | Hour | Rank | Actual Load
2008 | 8 | 1 | 17 | 1 | 17,623
2008 | 8 | 1 | 16 | 2 | 17,478
2008 | 8 | 1 | 18 | 3 | 17,463
2008 | 8 | 8 | 17 | 4 | 17,222
2008 | 8 | 8 | 18 | 5 | 17,184
P50 Forecast | Forecast Year
21,536 | 2020
21,253 | 2020
21,178 | 2020
21,108 | 2020
21,052 | 2020
ERCOT P50 Coincident Forecast for 2020

## Slide 41: ERCOT P50 Forecast
Forecast Year | Month | Day | Hour | COAST | EAST | FWEST | NCENT | NORTH | SCENT | SOUTH | WEST | ERCOT
2020 | 8 | 4 | 17 | 20,798 | 2,648 | 4,963 | 26,012 | 1,498 | 12,908 | 5,763 | 2,107 | 76,696
2020 | 8 | 1 | 17 | 21,536 | 2,742 | 4,932 | 25,197 | 1,455 | 12,143 | 5,711 | 1,927 | 75,643
2020 | 8 | 4 | 18 | 20,572 | 2,672 | 4,944 | 25,607 | 1,470 | 12,637 | 5,652 | 2,041 | 75,597
2020 | 8 | 4 | 16 | 20,712 | 2,664 | 4,920 | 25,525 | 1,465 | 12,465 | 5,728 | 2,037 | 75,515
2020 | 8 | 7 | 17 | 20,982 | 2,656 | 4,836 | 25,097 | 1,404 | 12,350 | 5,891 | 1,975 | 75,192
Historical Year | Month | Day | Hour | Rank | Actual Load
2008 | 8 | 1 | 17 | 1 | 17,623
2008 | 8 | 1 | 16 | 2 | 17,478
2008 | 8 | 1 | 18 | 3 | 17,463
2008 | 8 | 8 | 17 | 4 | 17,222
2008 | 8 | 8 | 18 | 5 | 17,184
P50 Forecast | Forecast Year
21,536 | 2020
21,253 | 2020
21,178 | 2020
21,108 | 2020
21,052 | 2020
ERCOT P50 Coincident Forecast for 2020

## Slide 42: ERCOT P50 Forecast
P50 Forecasts for each Weather Zone are mapped into a Historical Calendar by Rank
2008 Historical Calendar was selected
  Evaluated 2007 through 2018
  2008 had the least amount of diversity between Weather Zone peaks and ERCOT peak

## Slide 43: ERCOT P50 Coincident Peak Forecast
Chart: Year
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
2008 Coincident Factors | 76695.569 | 78298.6666 | 80107.5913 | 81593.2603 | 82982.0987 | 84193.342 | 85383.9337 | 86546.2076 | 87668.3732 | 88751.3167
Average Coincident Factors | 75890.5106 | 77488.0381 | 79297.5712 | 80783.5049 | 82172.0567 | 83382.8659 | 84573.0983 | 85735.0727 | 86856.9088 | 87939.5815
Minimum Coincident Factors | 74660.3714 | 76253.3345 | 78063.6858 | 79550.2554 | 80939.2548 | 82150.3199 | 83340.8902 | 84503.2827 | 85625.5366 | 86708.5876

## Slide 44: ERCOT P50 Coincident Peak Forecast
Chart: Year
| 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
Actual | 56068.0162 | 60029.6626 | 58483.7006 | 60212.6796 | 62202.8028 | 62114.7508 | 62102.9637 | 63407.1899 | 65713.4485 | 68317.6698 | 66557.7818 | 67252.9949 | 66464.0643 | 69620.4076 | 71092.6092 | 69496.2398 | 73308.1534 | 74665.5795
Forecast | 76695.569 | 78298.6666 | 80107.5913 | 81593.2603 | 82982.0987 | 84193.342 | 85383.9337 | 86546.2076 | 87668.3732 | 88751.3167

## Slide 45: ERCOT P50 Coincident Peak Forecast
Chart: Year
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
2019 LTLF | 76845.4656 | 78823.7416 | 80454.5979 | 82101.3718 | 83716.46 | 85327.0628 | 86940.3083 | 88507.6439 | 90020.6994 | 91509.1789
2020 LTLF | 76695.569 | 78298.6666 | 80107.5913 | 81593.2603 | 82982.0987 | 84193.342 | 85383.9337 | 86546.2076 | 87668.3732 | 88751.3167

## Slide 46: Coast P50 Peak Forecast
Chart: Year
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
2019 LTLF | 22084.9953 | 22584.8722 | 23089.2222 | 23597.1898 | 24098.6107 | 24597.5769 | 25094.7319 | 25576.8358 | 26041.8831 | 26497.3561
2020 LTLF | 21536.4211 | 21862.9327 | 22206.0532 | 22521.2584 | 22829.4103 | 23134.3416 | 23437.9834 | 23738.678 | 24030.3715 | 24314.4167

## Slide 47: East P50 Peak Forecast
Chart: Year
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
2019 LTLF | 2605.4906 | 2627.2996 | 2656.7706 | 2681.4289 | 2705.9982 | 2729.3485 | 2751.9179 | 2774.4113 | 2797.0594 | 2820.7324
2020 LTLF | 2741.5988 | 2762.0251 | 2788.8114 | 2807.4572 | 2825.3976 | 2841.7367 | 2858.7823 | 2876.7427 | 2893.2117 | 2909.4943

## Slide 48: North P50 Peak Forecast
Chart: Year
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
2019 LTLF | 1495.8035 | 1914.7682 | 1922.2792 | 1929.9148 | 1937.3636 | 1944.7129 | 1951.9765 | 1958.9829 | 1965.6889 | 1972.2284
2020 LTLF | 1497.547 | 1911.867 | 1915.6207 | 1919.5077 | 1923.5744 | 1927.6019 | 1931.5135 | 1935.5169 | 1939.7093 | 1944.1927

## Slide 49: South Central P50 Peak Forecast
Chart: Year
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
2019 LTLF | 12899.5125 | 13134.9362 | 13384.5573 | 13636.9906 | 13882.8458 | 14125.2174 | 14366.8989 | 14602.2775 | 14829.608 | 15053.061
2020 LTLF | 12908.0431 | 13049.5296 | 13206.4219 | 13375.9936 | 13544.3559 | 13706.9474 | 13864.4515 | 14016.3099 | 14162.2411 | 14301.2948

## Slide 50: South P50 Peak Forecast
Chart: Year
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
2019 LTLF | 6260.1376 | 6437.6276 | 6624.6645 | 6820.6348 | 7013.76 | 7207.988 | 7403.8736 | 7592.8571 | 7773.0996 | 7948.9804
2020 LTLF | 5992.0331 | 6080.2976 | 6734.2223 | 7069.7895 | 7322.2065 | 7424.6283 | 7526.4044 | 7626.8603 | 7723.8234 | 7818.2021

## Slide 51: West P50 Peak Forecast
Chart: Year
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
2019 LTLF | 2121.8146 | 2179.812 | 2242.1295 | 2306.0728 | 2367.8111 | 2428.8507 | 2488.651 | 2545.8662 | 2601.1886 | 2655.473
2020 LTLF | 2106.657 | 2153.2677 | 2207.6373 | 2262.9268 | 2319.2258 | 2373.0337 | 2424.6495 | 2478.5355 | 2534.1704 | 2591.4849

## Slide 52: North Central P50 Peak Forecast
Chart: Year
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
2019 LTLF | 26049.9898 | 26348.5456 | 26661.2889 | 26978.9924 | 27291.1004 | 27603.2997 | 27917.1607 | 28222.4987 | 28516.7715 | 28806.2
2020 LTLF | 26012.235 | 26302.7895 | 26620.8614 | 26965.1683 | 27309.9794 | 27647.9747 | 27978.173 | 28295.7904 | 28599.965 | 28889.8294

## Slide 53: Far West P50 Peak Forecast
Chart: Year
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
2019 LTLF | 4441.9583 | 4718.5 | 4996.9926 | 5275.2056 | 5546.0817 | 5817.7483 | 6093.9697 | 6364.6107 | 6627.7998 | 6888.243
2020 LTLF | 5022.7281 | 5301.0839 | 5553.5078 | 5798.4962 | 6035.8231 | 6265.351 | 6490.5893 | 6707.2612 | 6915.4144 | 7113.6241

## Slide 54: ERCOT P50 Coincident Peak Forecast
Chart: Year
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
2019 LTLF | 76845.4656 | 78823.7416 | 80454.5979 | 82101.3718 | 83716.46 | 85327.0628 | 86940.3083 | 88507.6439 | 90020.6994 | 91509.1789
2020 LTLF | 76695.569 | 78298.6666 | 80107.5913 | 81593.2603 | 82982.0987 | 84193.342 | 85383.9337 | 86546.2076 | 87668.3732 | 88751.3167

## Slide 55: ERCOT Annual Energy
Chart: Year
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
2019 LTLF | 401152.7199 | 413106.652 | 425665.1605 | 437595.1404 | 450426.0137 | 461024.6192 | 472723.596 | 484130.5215 | 496340.52 | 505944.0829
2020 LTLF | 401321.4125 | 411250.124 | 424830.7607 | 437920.9466 | 449969.4074 | 458262.8869 | 467416.1431 | 476372.8197 | 486219.7609 | 493415.2383

## Slide 56: ERCOT Annual Energy
Chart: Year
| 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
Actual | 279880.5312 | 284375.2214 | 288387.3917 | 298454.3809 | 304979.6733 | 306592.3592 | 310856.8551 | 307388.6171 | 318292.4722 | 333992.2576 | 325010.9182 | 331740.3591 | 340140.816 | 347496.4293 | 351401.9659 | 357260.0082 | 376229.6422 | 385271.5486
Forecast | 401321.4125 | 411250.124 | 424830.7607 | 437920.9466 | 449969.4074 | 458262.8869 | 467416.1431 | 476372.8197 | 486219.7609 | 493415.2383
November and December forecasted

## Slide 57
Assumptions and Challenges

## Slide 58: Assumptions
Inherent Levels from the Input Data of
  Appliance Stock and Energy Efficiency
  Demand Response
  4 CP Impact
  Behind-the-Meter DG
  Price Responsive Load
  Electric Vehicles

## Slide 59: Challenges
Weather Volatility
Economic Uncertainty
Policy Impacts

## Slide 60: Load Forecast Adjustments
Lubbock added to North Forecast from 2021 on
  Based on Lubbock’s Peak Forecast of its growth
“Fiber Services in Lubbock, TX.” About NTS, NTS Communications, Inc., 2018, www.ntscom.com/aboutnts/primary-locations/lubbock-tx.

## Slide 61: Load Forecast Adjustments
Rayburn added to East Forecast from 2020 on
  Based on Rayburn’s Actual Seasonal Peaks in 2019
“RCEC.” PROJECTS>OFFICE>RCEC, Alliance Architects, 2019, www.alliancearch.com/projects/office/rcec/.

## Slide 62: Load Forecast Adjustments
Adjustments added for Large Industrial Facilities
  Coast
    425 – 650 MW phased in over time
  South
    75 – 930 MW phased in over time
  Far West
    400 MW

## Slide 63
Active Models

## Slide 64: Ensemble of Active Models
Neural Network models based on linear and higher order nodes
Neural Network models based on a single linear node
Linear Regression representation of the Neural Network models
  Exact same variables and relationships
  Easier to share the model form with Market Participants
  Results are very close
Models are maintained for daily and hourly energy forecasting

## Slide 65
Weather Zone P50 and P90 Forecasts

## Slide 66: 90th Percentile (P90) Forecast
Coast 2020 Summer Forecasts
66
Rank | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | P50 | P90
1 | 21,257 | 21,208 | 21,081 | 21,499 | 21,099 | 21,858 | 21,485 | 22,220 | 22,656 | 21,458 | 21,172 | 22,031 | 21,660 | 21,074 | 21,290 | 21,536 | 22,394
2 | 21,166 | 20,502 | 20,895 | 21,413 | 20,756 | 21,384 | 21,266 | 22,151 | 21,250 | 21,244 | 21,132 | 21,947 | 21,406 | 21,025 | 21,257 | 21,253 | 22,029
3 | 21,083 | 20,421 | 20,883 | 21,358 | 20,716 | 21,277 | 21,254 | 22,128 | 21,236 | 21,211 | 21,099 | 21,589 | 21,356 | 20,902 | 21,153 | 21,178 | 21,804
4 | 20,996 | 20,404 | 20,603 | 21,225 | 20,641 | 21,250 | 21,170 | 22,096 | 21,152 | 21,210 | 21,001 | 21,555 | 21,348 | 20,841 | 21,131 | 21,108 | 21,771
5 | 20,834 | 20,382 | 20,495 | 21,131 | 20,591 | 21,156 | 21,170 | 22,040 | 21,119 | 21,188 | 20,972 | 21,545 | 21,299 | 20,792 | 21,062 | 21,052 | 21,743

## Slide 67: 90th Percentile (P90) Forecast
Coast 2020 Summer Forecasts
66
Rank | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | P50 | P90
1 | 21,257 | 21,208 | 21,081 | 21,499 | 21,099 | 21,858 | 21,485 | 22,220 | 22,656 | 21,458 | 21,172 | 22,031 | 21,660 | 21,074 | 21,290 | 21,536 | 22,394
2 | 21,166 | 20,502 | 20,895 | 21,413 | 20,756 | 21,384 | 21,266 | 22,151 | 21,250 | 21,244 | 21,132 | 21,947 | 21,406 | 21,025 | 21,257 | 21,253 | 22,029
3 | 21,083 | 20,421 | 20,883 | 21,358 | 20,716 | 21,277 | 21,254 | 22,128 | 21,236 | 21,211 | 21,099 | 21,589 | 21,356 | 20,902 | 21,153 | 21,178 | 21,804
4 | 20,996 | 20,404 | 20,603 | 21,225 | 20,641 | 21,250 | 21,170 | 22,096 | 21,152 | 21,210 | 21,001 | 21,555 | 21,348 | 20,841 | 21,131 | 21,108 | 21,771
5 | 20,834 | 20,382 | 20,495 | 21,131 | 20,591 | 21,156 | 21,170 | 22,040 | 21,119 | 21,188 | 20,972 | 21,545 | 21,299 | 20,792 | 21,062 | 21,052 | 21,743

## Slide 68: Coast P50 and P90 Peak Forecasts
Chart: Year
| 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
Actual | 18578.0722 | 19928.7248 | 19826.1816 | 20100.7586 | 20269.849 | 21256.1152
P50 | 21536.4211 | 21862.9327 | 22206.0532 | 22521.2584 | 22829.4103 | 23134.3416 | 23437.9834 | 23738.678 | 24030.3715 | 24314.4167
P90 | 22394.2924 | 22720.449 | 23063.6468 | 23379.283 | 23687.4659 | 23992.4338 | 24296.0876 | 24596.8905 | 24888.744 | 25172.8832

## Slide 69: East P50 and P90 Peak Forecasts
Chart: Year
| 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
Actual | 2324.9016 | 2463.9556 | 2493.8287 | 2415.8767 | 2565.6631 | 2554.0154
P50 | 2741.5988 | 2762.0251 | 2788.8114 | 2807.4572 | 2825.3976 | 2841.7367 | 2858.7823 | 2876.7427 | 2893.2117 | 2909.4943
P90 | 2852.4268 | 2872.8931 | 2899.6529 | 2918.2065 | 2936.138 | 2952.4629 | 2969.5371 | 2987.4846 | 3003.9395 | 3020.2152

## Slide 70: Far West P50 and P90 Peak Forecasts
Chart: Year
| 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
Actual | 2688.0037 | 2811.8407 | 2908.9704 | 3164.1864 | 3655.0145 | 4307.5529
P50 | 5022.7281 | 5301.0839 | 5553.5078 | 5798.4962 | 6035.8231 | 6265.351 | 6490.5893 | 6707.2612 | 6915.4144 | 7113.6241
P90 | 5408.208 | 5947.3342 | 6281.9135 | 6597.8209 | 6906.8237 | 7207.6798 | 7507.0577 | 7790.6359 | 8079.9352 | 8354.6464

## Slide 71: North P50 and P90 Peak Forecasts
Chart: Year
| 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
Actual | 1407.7908 | 1451.5364 | 1440.1835 | 1393.5089 | 1521.8453 | 1476.3299
P50 | 1497.547 | 1911.867 | 1915.6207 | 1919.5077 | 1923.5744 | 1927.6019 | 1931.5135 | 1935.5169 | 1939.7093 | 1944.1927
P90 | 1603.8593 | 2020.0674 | 2023.8398 | 2027.73 | 2031.8007 | 2035.8236 | 2039.7353 | 2043.7429 | 2047.9458 | 2052.4347

## Slide 72: North Central P50 and P90 Peak Forecasts
Chart: Year
| 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
Actual | 23445.6124 | 24580.6459 | 25282.3165 | 24313.2101 | 26499.241 | 25493.7914
P50 | 26012.235 | 26302.7895 | 26620.8614 | 26965.1683 | 27309.9794 | 27647.9747 | 27978.173 | 28295.7904 | 28599.965 | 28889.8294
P90 | 27251.7349 | 27541.6259 | 27858.7888 | 28202.7424 | 28547.7155 | 28885.8835 | 29216.375 | 29534.378 | 29838.9805 | 30129.1284

## Slide 73: South P50 and P90 Peak Forecasts
Chart: Year
| 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
Actual | 5352.2159 | 5455.4528 | 5786.8259 | 5845.2837 | 5791.2531 | 6039.7135
P50 | 5992.0331 | 6080.2976 | 6734.2223 | 7069.7895 | 7322.2065 | 7424.6283 | 7526.4044 | 7626.8603 | 7723.8234 | 7818.2021
P90 | 6140.1597 | 6228.4559 | 6882.5221 | 7218.0466 | 7470.4684 | 7572.87 | 7674.6432 | 7775.0697 | 7871.9923 | 7966.3512

## Slide 74: South Central P50 and P90 Peak Forecasts
Chart: Year
| 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
Actual | 11452.2257 | 12032.5532 | 12344.8416 | 11970.2041 | 12886.8971 | 12784.8579
P50 | 12908.0431 | 13049.5296 | 13206.4219 | 13375.9936 | 13544.3559 | 13706.9474 | 13864.4515 | 14016.3099 | 14162.2411 | 14301.2948
P90 | 13647.87 | 13789.1031 | 13945.4941 | 14114.9409 | 14283.445 | 14446.1825 | 14603.8375 | 14755.8623 | 14901.9912 | 15041.1866

## Slide 75: West P50 and P90 Peak Forecasts
Chart: Year
| 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
Actual | 1852.9276 | 1883.889 | 1899.0862 | 1901.9406 | 2083.5791 | 2117.3991
P50 | 2106.657 | 2153.2677 | 2207.6373 | 2262.9268 | 2319.2258 | 2373.0337 | 2424.6495 | 2478.5355 | 2534.1704 | 2591.4849
P90 | 2213.4092 | 2260.1821 | 2314.7841 | 2370.0923 | 2426.3742 | 2480.0257 | 2531.6598 | 2585.6499 | 2641.3545 | 2698.7561

## Slide 76: Questions?

## Slide 77: Slide 28 Normal Weather (P50) Forecast
Chart: Coast 2020 Summer Peak Forecasts
| 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018
 | 21257.3872 | 21208.0153 | 21080.7538 | 21499.2553 | 21098.5938 | 21857.6111 | 21484.7698 | 22219.7904 | 22656.0454 | 21457.6694 | 21171.7986 | 22030.5948 | 21659.7427 | 21074.4763 | 21289.8129

## Slide 78: Slide 32 Normal Weather (P50) Forecast
Chart: Coast 2020 Summer Peak Forecasts
| 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | Highest | Lowest | P50
 | 21257.3872 | 21208.0153 | 21080.7538 | 21499.2553 | 21098.5938 | 21857.6111 | 21484.7698 | 22219.7904 | 22656.0454 | 21457.6694 | 21171.7986 | 22030.5948 | 21659.7427 | 21074.4763 | 21289.8129 | 22656.0454 | 21074.4763 | 21536.4211

## Slide 79: Slide 43 ERCOT P50 Coincident Peak Forecast
Chart: Year
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
2008 Coincident Factors | 76695.569 | 78298.6666 | 80107.5913 | 81593.2603 | 82982.0987 | 84193.342 | 85383.9337 | 86546.2076 | 87668.3732 | 88751.3167
Average Coincident Factors | 75890.5106 | 77488.0381 | 79297.5712 | 80783.5049 | 82172.0567 | 83382.8659 | 84573.0983 | 85735.0727 | 86856.9088 | 87939.5815
Minimum Coincident Factors | 74660.3714 | 76253.3345 | 78063.6858 | 79550.2554 | 80939.2548 | 82150.3199 | 83340.8902 | 84503.2827 | 85625.5366 | 86708.5876

## Slide 80: Slide 44 ERCOT P50 Coincident Peak Forecast
Chart: Year
| 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
Actual | 56068.0162 | 60029.6626 | 58483.7006 | 60212.6796 | 62202.8028 | 62114.7508 | 62102.9637 | 63407.1899 | 65713.4485 | 68317.6698 | 66557.7818 | 67252.9949 | 66464.0643 | 69620.4076 | 71092.6092 | 69496.2398 | 73308.1534 | 74665.5795
Forecast | 76695.569 | 78298.6666 | 80107.5913 | 81593.2603 | 82982.0987 | 84193.342 | 85383.9337 | 86546.2076 | 87668.3732 | 88751.3167

## Slide 81: Slides 45 and 54 ERCOT P50 Coincident Peak Forecast
Chart: Year
| 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
2019 LTLF | 76845.4656 | 78823.7416 | 80454.5979 | 82101.3718 | 83716.46 | 85327.0628 | 86940.3083 | 88507.6439 | 90020.6994 | 91509.1789
2020 LTLF | 76695.569 | 78298.6666 | 80107.5913 | 81593.2603 | 82982.0987 | 84193.342 | 85383.9337 | 86546.2076 | 87668.3732 | 88751.3167

## Slide 82: Slide 56 ERCOT Annual Energy
Chart: Year
| 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
Actual | 279880.5312 | 284375.2214 | 288387.3917 | 298454.3809 | 304979.6733 | 306592.3592 | 310856.8551 | 307388.6171 | 318292.4722 | 333992.2576 | 325010.9182 | 331740.3591 | 340140.816 | 347496.4293 | 351401.9659 | 357260.0082 | 376229.6422 | 385271.5486
Forecast | 401321.4125 | 411250.124 | 424830.7607 | 437920.9466 | 449969.4074 | 458262.8869 | 467416.1431 | 476372.8197 | 486219.7609 | 493415.2383
December estimated

## Slide 83: Slide 68 Coast P50 and P90 Peak Forecasts
Chart: Year
| 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
Actual | 18578.0722 | 19928.7248 | 19826.1816 | 20100.7586 | 20269.849 | 21256.1152
P50 | 21536.4211 | 21862.9327 | 22206.0532 | 22521.2584 | 22829.4103 | 23134.3416 | 23437.9834 | 23738.678 | 24030.3715 | 24314.4167
P90 | 22394.2924 | 22720.449 | 23063.6468 | 23379.283 | 23687.4659 | 23992.4338 | 24296.0876 | 24596.8905 | 24888.744 | 25172.8832

## Slide 84: Slide 69 East P50 and P90 Peak Forecasts
Chart: Year
| 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
Actual | 2324.9016 | 2463.9556 | 2493.8287 | 2415.8767 | 2565.6631 | 2554.0154
P50 | 2741.5988 | 2762.0251 | 2788.8114 | 2807.4572 | 2825.3976 | 2841.7367 | 2858.7823 | 2876.7427 | 2893.2117 | 2909.4943
P90 | 2852.4268 | 2872.8931 | 2899.6529 | 2918.2065 | 2936.138 | 2952.4629 | 2969.5371 | 2987.4846 | 3003.9395 | 3020.2152

## Slide 85: Slide 70 Far West P50 and P90 Peak Forecasts
Chart: Year
| 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
Actual | 2688.0037 | 2811.8407 | 2908.9704 | 3164.1864 | 3655.0145 | 4307.5529
P50 | 5022.7281 | 5301.0839 | 5553.5078 | 5798.4962 | 6035.8231 | 6265.351 | 6490.5893 | 6707.2612 | 6915.4144 | 7113.6241
P90 | 5408.208 | 5947.3342 | 6281.9135 | 6597.8209 | 6906.8237 | 7207.6798 | 7507.0577 | 7790.6359 | 8079.9352 | 8354.6464

## Slide 86: Slide 71 North P50 and P90 Peak Forecasts
Chart: Year
| 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
Actual | 1407.7908 | 1451.5364 | 1440.1835 | 1393.5089 | 1521.8453 | 1476.3299
P50 | 1497.547 | 1911.867 | 1915.6207 | 1919.5077 | 1923.5744 | 1927.6019 | 1931.5135 | 1935.5169 | 1939.7093 | 1944.1927
P90 | 1603.8593 | 2020.0674 | 2023.8398 | 2027.73 | 2031.8007 | 2035.8236 | 2039.7353 | 2043.7429 | 2047.9458 | 2052.4347

## Slide 87: Slide 72 North Central P50 and P90 Peak Forecasts
Chart: Year
| 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
Actual | 23445.6124 | 24580.6459 | 25282.3165 | 24313.2101 | 26499.241 | 25493.7914
P50 | 26012.235 | 26302.7895 | 26620.8614 | 26965.1683 | 27309.9794 | 27647.9747 | 27978.173 | 28295.7904 | 28599.965 | 28889.8294
P90 | 27251.7349 | 27541.6259 | 27858.7888 | 28202.7424 | 28547.7155 | 28885.8835 | 29216.375 | 29534.378 | 29838.9805 | 30129.1284

## Slide 88: Slide 73 South P50 and P90 Peak Forecasts
Chart: Year
| 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
Actual | 5352.2159 | 5455.4528 | 5786.8259 | 5845.2837 | 5791.2531 | 6039.7135
P50 | 5992.0331 | 6080.2976 | 6734.2223 | 7069.7895 | 7322.2065 | 7424.6283 | 7526.4044 | 7626.8603 | 7723.8234 | 7818.2021
P90 | 6140.1597 | 6228.4559 | 6882.5221 | 7218.0466 | 7470.4684 | 7572.87 | 7674.6432 | 7775.0697 | 7871.9923 | 7966.3512

## Slide 89: Slide 74 South Central P50 and P90 Peak Forecasts
Chart: Year
| 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
Actual | 11452.2257 | 12032.5532 | 12344.8416 | 11970.2041 | 12886.8971 | 12784.8579
P50 | 12908.0431 | 13049.5296 | 13206.4219 | 13375.9936 | 13544.3559 | 13706.9474 | 13864.4515 | 14016.3099 | 14162.2411 | 14301.2948
P90 | 13647.87 | 13789.1031 | 13945.4941 | 14114.9409 | 14283.445 | 14446.1825 | 14603.8375 | 14755.8623 | 14901.9912 | 15041.1866

## Slide 90: Slide 75 West P50 and P90 Peak Forecasts
Chart: Year
| 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029
Actual | 1852.9276 | 1883.889 | 1899.0862 | 1901.9406 | 2083.5791 | 2117.3991
P50 | 2106.657 | 2153.2677 | 2207.6373 | 2262.9268 | 2319.2258 | 2373.0337 | 2424.6495 | 2478.5355 | 2534.1704 | 2591.4849
P90 | 2213.4092 | 2260.1821 | 2314.7841 | 2370.0923 | 2426.3742 | 2480.0257 | 2531.6598 | 2585.6499 | 2641.3545 | 2698.7561