## Sheet1
TDSP comments |  | ERCOT Comments
1 | Clarify DSP authority to require DGR to follow DSp voltage requirements
2 | Clarify language on outage notifications.
| a. There are no notification timelines specified, either for the DSP notification to the DGR, or for the DGR notification to ERCOT. Is this preferred? | tbd
| b. Will the DSP be responsible for notifying the DGR directly for any planned transmission outages that affect the DGR (vs normal entry into the ERCOT Outage Scheduler only)? | not anticipated.
c. ERCOT’s Nov 5 workshop slide 7 states the DSP must notify the Resource Entity for the DGR. Should the DSP be notifying the DGR’s QSE?
3 | Confirm reconfiguring feeder notifications are not required if path is not impacted for DGR
a. Normal construction for new customers may only affect a portion of load on the feeder and not the DGR itself (i.e., construction is not altering the electrical path to the DGR).
b. We support ERCOT’s proposed Protocol 3.8.7(3) in which reconfiguration of a feeder altering the electrical path to the DGR would only be subject to notification if the reconfiguration will be more than 60 days in duration.
4 | Support idea of PGRR for process
| a. ERCOT should define the minimum requirements the DGR must meet for the process to begin, a defined set (with some initial flexibility) of DSP-performed studies, and defined timelines. | To be discussed at 12/11 meeting
| b. There is a learning curve (planning and operational) involved with DGRs; study requirements are going to evolve and improve over time. DSPs may potentially add studies that are not contemplated now, or may waive studies that are not needed. | noted
| c. It would be useful for ERCOT to require the DGR to specify which types of AS it will provide, so this can be considered in the DSP studies. Some types of AS may have more significant impacts on the distribution system (e.g., FRRS) and therefore require more extensive studies, while other types of AS may have a lesser impact and are less study-intensive. | To be discussed at 12/11 meeting
| d. If the DGR elects to provide additional types of AS, it must notify ERCOT and the DSP, either of which may require additional studies prior to the DGR offering the new AS. | To be discussed at 12/11 meeting
| e Planning for the long term risks and benefits of DGR and their cumulative impacts on the utility system needs to be incorporated into ERCOT Protocols and Guides, and TDSP procedures. | Section added in the DGR Process
I Example: Transmission contingencies that cause DGR to react, or other conditions that require technical studies and coordination across the T&D boundary.
5 | ERCOT system doesn’t include Distribution will need to add in that if we intend to include it.
| a. Protocol Section 2 definition: “The interconnected power system that is under the jurisdiction of the PUCT and that is not synchronously interconnected with either the Eastern Interconnection or the Western Electricity Coordinating Council.” | To be discussed at 12/11 meeting
| b. Where the word “transmission” before the term “ERCOT system” was struck in ERCOT’s proposed Protocol changes for DGR (for example, 3.10.7.2(1)), we suggest the following: “ERCOT system or the distribution system”. | To be discussed at 12/11 meeting
6 | Protocol 3.10.7.2(3), at the end of the long first sentence “Each Resource Entity representing a Distribution Generation Resource…and any additional information and telemetry as required by ERCOT,” please add “and the interconnecting DSP”.
7 | If the desired completion of the protocol changes is summer/fall 2020 and the expected certifications for UL 1741-2020 will not be available until fall 2020 or winter 2020/2021, who is liable for any failed operation during the time the DGR is not certified to operate in the stated ranges of voltage and frequency set points? | ERCOTs understanding is the owner of the equipment is liable.
b. Although the DSP may be able to test for DGR functionality in the stated ranges, this should not be taken as a certification in any way that a DGR will always operate as desired in the tested range.
8 | It is understood that the desire is to have a DGR remain off any load shed feeders for the lifetime of a project. | may need to be addressed in a future NPRR
| a. Does this also include Remedial Action Schemes for transmission lines? | may need to be addressed in a future NOGRR
b. If a DGR is temporarily moved to another feeder, does the alternate feeder (attached to the same bus) have to be a non-load shed feeder for the DGR to remain in operation
Example: Feeder breaker maintenance
We propose the DGR should be allowed to be moved to a load shed feeder if it resides there for less than 30 days.
| c. Long term, if DGRs proliferate it will be impractical to completely prohibit them from residing on load shed feeders. If a DGR connects to a feeder that becomes a load shed feeder in the future, the DSP would notify the DGR, and it can become SODG. | agreed
| d. Impacts to load shed considerations needs further vetting, not only due to the anticipated proliferation of DGRs but what are considered as critical loads may also need to be reviewed. | may need to be addressed in a future NPRR
9 | We propose that ERCOT establish a minimum size for DGRs of 2MW. | ERCOT proposes 1 MW threshold and there is at least 1 project submittal for less than 2 MW
TAEBA comments
1 | While ERCOT’s commitment to work efficiently and quickly on the issues raised by the DGR Market Notice is helpful, it still leaves prospective DGR installers, owners, and operators without the certainty they need to make business decisions. | agreed
2 | We therefore agree with ERCOT’s proposal to continue to work through these issues through workshops to allow for a more nimble, accelerated process, and we further encourage ERCOT to explore ways to expedite the development and approval of the relevant Nodal Protocol Revision Request (NPRR), Planning Guide Revision Request (PGRR), and Nodal Operating Guide Revision Request (NOGRR).
KCE Comments
1 | AVR needs to be coordinated with DSP
2 | Given that it is infeasible for KCE to achieve the proposed VRT requirements, and inverters that can do so are not yet commercially-available, KCE respectfully recommends that ERCOT pursue one of the following options: | ERCOT proposes revised settings that commercially available equipment can meet.
a. Grandfather in DGR projects installed prior to the commercial availability of inverters that can meet the proposed VRT requirements by allowing such projects to meet the current VRT requirements of NERC PRC-024-2; or
b. Revise the proposed UV1 Minimum Ride-Through time down from 21 seconds to five seconds (in conformance with the current VRT requirements of NERC PRC-024-2.)
Shell comments
1 | Clarify the registration requirements for >1MW and <10 MW.
ERCOT agrees and language has been revised to reflect (if necessary)
Either further clarification is needed, or ERCOT disagrees - Item needs to be resolved.
A comment or observation. There don’t seem to be any language changes needed to be resolved, but may require future action