## TransmissonUpgrades
Project |  | Project Description | From Bus | To Bus | From TSP | To TSP | Minimum Summer Normal and Emergency Ratings (RATE A/B) (MVA) Modeled in Study Case | Assumed Miles | Common = Project is needed regardless of import options | Reliability Need
Upgrades for N-0
1 | Added 1,860 Mvar reactive devices | Dynamic Reactive Devices such as SVC, STATCOM and Syncronous Condenser at Clearfork | 79650 |  | ONCOR_ED |  | 300 Mvar |  | Common | Voltage Collapse
|  | Dynamic Reactive Devices such as SVC, STATCOM and Syncronous Condenser at Riverton | 11084 |  | ONCOR_ED |  | 300 Mvar |  | Common | Voltage Collapse
|  | Dynamic Reactive Devices such as SVC, STATCOM and Syncronous Condenser at Wolf | 21013 |  | ONCOR_ED |  | 300 Mvar |  | Common | Voltage Collapse
|  | Dynamic Reactive Devices such as SVC, STATCOM and Syncronous Condenser at Barilla Draw | 38065 |  | TNMP_TSP |  | 300 Mvar |  | Common | Voltage Collapse
|  | Dynamic Reactive Devices such as SVC, STATCOM and Syncronous Condenser at Faulkner | 38124 |  | TNMP_TSP |  | 300 Mvar |  | Common | Voltage Collapse
|  | Owl Hills 138-kV Capacitors | 11090 |  | ONCOR_ED |  | 110 Mvar |  | Common | Voltage Collapse
|  | Coalson Draw with DRD | 11078 |  | ONCOR_ED |  | 250 Mvar |  | Common | Voltage Collapse
2 | Tapped the new 345-kV Wolf station to the Odessa/Moss -Riverton 345-kV double circuit lines (TPIT 46094, Tier 3, Dec 2020) | New Wolf 345/138-kV substation | 21013 |  | ONCOR_ED |  | 2988/2988 (Line Ratings) |  | Common | Voltage Collapse
|  | Two 345/138-kV Xfrms at Wolf | 21013 |  | ONCOR_ED |  | 750/750 |  | Common | Voltage Collapse
3 | 345-kV import path is also needed for N-0. |  | n/a | n/a | n/a | n/a |  |  | Common | Voltage Collapse
4 | Convert AEP 69-kV line Barrilla - Hoefs Road - Verhalen - Saragosa to 138-kV |  | 60385 | 60716 | AEP_TNC | AEP_TNC | 483/483 | 33.78 | Common | Voltage Collapse
5 | Convert TNMP 69-kV system from Wink to IH20 to 138-kV. |  |  |  | TNMP_TSP | TNMP_TSP |  |  | Common | Approved Tier 2 RPG project.
6 | Convert ONCOR 69-kV line Yucca - Royalty - Coyanosa - Wolfcamp to 138-kV |  | 1009 | 1242 | ONCOR_ED | ONCOR_ED | 614/614 | 46.9 | Common | Yucca - Royalty - Coyanosa 69-kV
7 | Upgrade the Gemsbok to Gemsbok Autonomous Crypto 138-kV line |  | 38107 | 38109 | TNMP_TSP | TNMP_TSP | 614/614 | 1.35 | Common | Gemsbok to Gemsbok Autonomous Crypto 138-kV
8 | Tap the Wolf - Riverton 345-kV double circuit at Quarry Field, and add two 345/138-kV autotransformer at Quarry Field | Quarry Field 345-kV station | 11188 |  | ONCOR_ED |  |  |  | Common | Both Riverton 345/138-kV transformers
|  | Two 345/138-kV Xfrms at Quarry Field | 11188 |  | ONCOR_ED |  | 750/750 |  | Common
9 | Upgrade Quail Switch - Odessa 345-kV line |  | 11016 | 11028 | ONCOR_ED | ONCOR_ED | 1521/1784 | 0.9 | Common | Quail Switch - Odessa 345-kV
10 | Upgrade the Solstice - Hayter 138-kV line |  | 60385 | 78925 | AEP_TNC | AEP_TNC | 614/614 | 1.5 | Common | Solstice - Hayter 138-kV
Upgrades for N-1
11 | Build a new 345/138-kV OwlHill station with two 345/138-kV transformers, and add a new single circuit 345-kV line from Riverton to 345-kV OwlHill station | OwlHill 345/138-kV station | 211090 |  | ONCOR_ED |  | 2988/2988 (Line Ratings) |  | Common | Riverton 345/138-kV transformer1/transformer2; There're also unsolved contingencies along the Riverton - OwlHill area
|  | Two 345/138-kV Xfrms at OwlHill | 211090 |  | ONCOR_ED |  | 750/750 |  | Common
|  | Single 345-kV line from Riverton to OwlHill | 11084 | 211090 | ONCOR_ED | ONCOR_ED | 2988/2988 | 20.27 | Common
12 | Tap the new Megan station to the Solstice - Sand Lake 345-kV double-circuit lines, and install two new 345/138-kV transformers at the new Megan station | New 345/138-kV Megan station | 38083 |  | TNMP_TSP |  | 2988/2988 (Line Ratings) |  | Common | Voltage Collapse
|  | Two 345/138-kV Xfrms at new Megan station | 38083 |  | TNMP_TSP |  | 750/750 |  | Common
13 | Build a new 138-kV line from Saragosa to Faulkner |  | 60716 | 38124 | AEP_TNC | TNMP_TSP | 614/614 | 18 | Common | a. IH20 - SALT DRAW TAP TNP - SADDLEBACK 138-kV b. TNMP Pecos - Reeves Tap 138-kV
14 | Upgrade the 138-kV line from Hayter to Remeranch |  | 78925 | 99900 | AEP_TNC | AEP_TNC | 614/614 | 14.15 | Common | Hayter - Remeranch 138-kV
15 | Rio Pecos to Fort Stockton Upgrade: Upgrade the 138-kV lines from Rio Pecos - Lynx - TNMP 16th St - Fort Stockton | Rio Pecos - Lynx 138-kV Ckt2 | 6601 | 60400 | AEP_TNC | AEP_TNC | 483/483 | 1.91 | Common | a. 16TH STREET TNP - WOODWARD 2 138-kV b. Fort Stockton - AIRPORT TNP 138-kV c. 16TH STREET TNP - AIRPORT TNP 138-kV d. Fort Stockton - TOMBSTONE 138-kV
|  | Lynx - Tombstone - Fort Stockton 138-kV | 60400 | 6630 | AEP_TNC | AEP_TNC | 483/483 | 35.31 | Common
|  | Lynx - 16th Street TNP 138-kV | 60400 | 38310 | AEP_TNC | TNMP_TSP | 483/483 | 31.78 | Common
|  | 16th Street TNP - Airport TNP 138-kV | 38310 | 38340 | TNMP_TSP | TNMP_TSP | 483/483 | 2.78 | Common
|  | Airport TNP 138kV - Fort Stockton 138-kV | 38340 | 6630 | TNMP_TSP | AEP_TNC | 483/483 | 2.8 | Common
16 | Convert the existing Fort Stockton - Conoco Comp station - Conoco Rgec 69-kV line to 138-kV. Move the 138/69-kV transformer from Fort Stockton to Conoco Comp station | Fort Stockton-Conoco Comp | 6628 | 6663 | AEP_TNC | AEP_TNC | 614/614 | 13.97 | Common | Voltage Collapse
|  | Conoco Comp-Conoco Rgec | 6663 | 76663 | AEP_TNC | LCRA TSC | 614/614 | 11.12 | Common
17 | Build a new 138-kV line from Conoco Rgec to TNMP 16th street |  | 76663 | 38310 | LCRA TSC | TNMP_TSP | 483/483 | 22 | Common | Voltage Collapse
18 | Build a new 138-kV line from Remeranch to Saragosa |  | 99900 | 6652 | AEP_TNC | AEP_TNC | 483/483 | 26.5 | Common | Voltage Collapse
19 | Upgrade Morgan Creek - Tonkawa 345-kV line |  | 1030 | 11048 | ONCOR_ED | ONCOR_ED | 1792/1792 | 21.3 | Common | Morgan Creek - Tonkawa 345-kV line
20 | Upgrade Morgan Creek - Longshore 345-kV line |  | 1030 | 1058 | ONCOR_ED | ONCOR_ED | 1792/1792 | 36.5 | Needed for an option with new Bearkat - North McCamey line | Morgan Creek - Longshore 345-kV line
21 | Upgrade Midland East - Falcon Seaboard 345-kV |  | 1021 | 1025 | ONCOR_ED | ONCOR_ED | 1792/1792 | 48.4 | Common | Midland East - Falcon Seaboard 345-kV
22 | Upgrade Saddleback - Salt Draw Tap 138-kV |  | 38058 | 38080 | TNMP_TSP | TNMP_TSP | 717/717 | 0.5 | Option 5 | Saddleback - Salt Draw Tap 138-kV
23 | Build new 138-kV double circuit from the new Megan station to Saddleback |  | 38080 | 38055 | TNMP_TSP | TNMP_TSP | 614/614 | 6.2 | Common | Needed to connect the new Megan 345-kV source to the 138-kV system
24 | Upgrade Salt Draw Tap - IH20 138-kV |  | 38055 | 38045 | TNMP_TSP | TNMP_TSP | 717/717 | 4.9 | Option 5 | Salt Draw Tap - IH20 138-kV
25 | Build new 138-kV double circuit from the new Megan station to Faulkner |  | 38080 | 38124 | TNMP_TSP | TNMP_TSP | 614/614 | 24.2 | Common | Needed to connect the new Megan 345-kV source to the 138-kV system
26 | Upgrade Morgan Creek - Falcon Seaboard 345-kV |  | 1030 | 1025 | ONCOR_ED | ONCOR_ED | 1792/1792 | 36.2 | Needed for Options 5 & 9 | Morgan Creek - Falcon Seaboard 345-kV
27 | Upgrade Longshore - Midessa 345-kV |  | 1058 | 1125 | ONCOR_ED | ONCOR_ED | 1792/1792 | 48 | Needed for Option 9 | Longshore - Midessa 345-kV
28 | Upgrade Midland East - Midland County NW 345-kV |  | 1022 | 1185 | ONCOR_ED | ONCOR_ED | 1792/1792 | 17.2 | Needed for Options 5 & 9 | Midland East - Midland County NW 345-kV
29 | 2nd 345-kV Circuit from Big Hill to Bakersfield |  | 76003 | 76002 | LCRA TSC | LCRA TSC | 1521/1784 | 111.42 | Option 1
| 2nd 345-kV Circuit from Bakersfield to North McCamey |  | 76002 | 76000 | LCRA TSC | LCRA TSC | 1521/1784 | 16.27
| 2nd 345-kV Circuit from North McCamey to Odessa |  | 76000 | 11028 | LCRA TSC | ONCOR_ED | 1521/1784 | 58.72
| North McCamey - Megan 345-kV Double Ckt |  | 76000 | 38083 | LCRA TSC | TNMP_TSP | 2564/2564 | 78
30 | Faraday - Lamesa 345-kV Single Ckt |  | 59905 | 991163 | WETT | ONCOR_ED | 2564/2564 | 34.2 | Option 2
| Lamesa - Clearfork 345-kV Single Ckt |  | 991163 | 79650 | ONCOR_ED | ONCOR_ED | 2564/2564 | 76.8
| Clearfork - Riverton 345-kV Single Ckt |  | 79650 | 11084 | ONCOR_ED | ONCOR_ED | 2564/2564 | 82
31 | Faraday - Lamesa 345-kV Double Ckt |  | 59905 | 991163 | WETT | ONCOR_ED | 2564/2564 | 34.2 | Option 4
| Lamesa - Clearfork 345-kV Double Ckt |  | 991163 | 79650 | ONCOR_ED | ONCOR_ED | 2564/2564 | 76.8
| Clearfork - Riverton 345-kV Double Ckt |  | 79650 | 11084 | ONCOR_ED | ONCOR_ED | 2564/2564 | 82
32 | Bearkat - North McCamey 345-kV Single Ckt |  | 59903 | 76000 | WETT | LCRA TSC | 2564/2564 | 70.8 | Option 3
| North McCamey - Megan 345-kV Single Ckt |  | 76000 | 38083 | LCRA TSC | TNMP_TSP | 2564/2564 | 78
33 | Bearkat - North McCamey 345-kV Double Ckt |  | 59903 | 76000 | WETT | LCRA TSC | 2564/2564 | 70.8 | Option 5
| North McCamey - Megan 345-kV Double Ckt |  | 76000 | 38083 | LCRA TSC | TNMP_TSP | 2564/2564 | 78
34 | Bearkat - North McCamey 345-kV Double Ckt |  | 59903 | 76000 | WETT | LCRA TSC | 2564/2564 | 70.8 | Option 6
| North McCamey - Sand Lake 345-kV Double Ckt |  | 76000 | 11096 | LCRA TSC | ONCOR_ED | 2564/2564 | 93.6
35 | North McCamey - Megan 345-kV Double Ckt |  | 76000 | 38083 | LCRA TSC | TNMP_TSP | 2564/2564 | 78 | Option 7
| Red Creek - North McCamey 345-kV Double Ckt |  | 6444 | 76000 | AEP_TNC | LCRA TSC | 2564/2564 | 138
36 | 1,200 MW HVDC line (VSC) from Abernathy to Riverton |  | 79506 | 11084 | ONCOR_ED | ONCOR_ED | 1200 | 240.24 | Option 8
37 | 1,200 MW HVDC line (VSC) from Howard Road to Bakersfield |  | 5056 | 76002 | CPS_TSP | LCRA TSC | 1200 | 302 | Option 9
| North McCamey - Megan 345-kV Double Ckt |  | 76000 | 38083 | LCRA TSC | TNMP_TSP | 2564/2564 | 78
38 | Howard Road - Bakersfield 765-kV Single Ckt + Transformers | Howard Road - Bakersfield 765-kV single Ckt line | 5056 | 76002 | CPS_TSP | LCRA TSC | 3975/3975 | 302 | Option 10
|  | Two 765/345-kV Xfrms at Howard Road | 5056 |  | CPS_TSP |  | 1500/1500
|  | Two 765/345-kV Xfrms at Bakersfield |  | 76002 |  | LCRA TSC | 1500/1500
| North McCamey - Megan 345-kV Double Ckt |  | 76000 | 38083 | LCRA TSC | TNMP_TSP | 2564/2564 | 78
39 | Build a new 138-kV line from Elcor to Faulkner |  | 11198 | 38124 | ONCOR_ED | TNMP_TSP | 614/614 | 36 | Common | Customer Needs
40 | Convert Riverton - Sand Lake 138-kV to 345-kV |  | 11084 | 11096 | ONCOR_ED | ONCOR_ED | 2988/2988 | 40 | Option 6g
41 | Build a new Riverton - Sand Lake 138-kV line |  | 11083 | 11097 | ONCOR_ED | ONCOR_ED | 765/765
42 | Upgrade Odessa - Wolf 138-kV |  | 1027 | 1013 | ONCOR_ED | ONCOR_ED | 614/614 | 44.4 | Needed for Option 6g | Odessa - Wolf 138-kV