## Site Audit Checklist
Site/Facility: ERCOT EPS Site Audit Date:
Design Proposal Approval Date: Project#: Meter Point: Auditor:
Design Proposal/Facility Details Information
Facility Details
NUM. | QUESTION | PROTOCOL | RESOURCE TYPE | CHECK METHOD | MEETS REQ. | COMMENT | FOLLOW UP
1.1.1 | Does One Line accurately reflect the EPS Metering configuration including breakers/by-passes that would affect the metered energy flow? | Protocol 10.4.2(1), SMOG Section 3.2.1(1)(b), 3.2.1(1)(c) and 3.2.3(1)(h) | Approved EPS Design Proposal | Visual | TRUE |  | FALSE
1.1.2 | Do breakers exist where one line diagram indicates? | Protocol 10.4.2(1), SMOG Section 3.2.1(1)(b), 3.2.1(1)(c) and 3.2.3(1)(h) | Approved EPS Design Proposal | Visual | TRUE |  | FALSE
1.1.3 | Are CT's located as one line diagram indicates? | Protocol 10.4.2(1), SMOG Section 3.2.1(1)(b), 3.2.1(1)(c) and 3.2.3(1)(h) | Approved EPS Design Proposal | Visual | TRUE |  | FALSE
1.1.4 | Are VT's located as one line diagram indicates? | Protocol 10.4.2(1), SMOG Section 3.2.1(1)(b), 3.2.1(1)(c) and 3.2.3(1)(h) | Approved EPS Design Proposal | Visual | TRUE |  | FALSE
1.1.5 | Do three lines and one line drawings match one another? | Protocol 10.4.2(1), SMOG Section 3.2.1(1)(b), 3.2.1(1)(c) and 3.2.3(1)(h) | Approved EPS Design Drawing | TDSP Documentation | TRUE |  | FALSE
1.1.6 | CT Ratio-Does design approved ratio match existing CT ratio? If dual ratio, is the connected ratio correct? | Protocol 10.4.2(1), SMOG Section 3.2.1(1)(b), 3.2.1(1)(c) and 3.2.3(1)(h) | Equipment Access | Visual | TRUE |  | FALSE
1.1.7 | PT Ratio-Does design approval ratio match existing VT ratio? If dual ratio, is the ratio connected correct? | Protocol 10.4.2(1), SMOG Section 3.2.1(1)(b), 3.2.1(1)(c) and 3.2.3(1)(h) | Equipment Access | Visual | TRUE |  | FALSE
1.1.8 | VT Polarity-Are polarity's oriented the correct direction with reference to the design proposal? | Protocol 10.4.2(1), SMOG Section 3.2.1(1)(b), 3.2.1(1)(c) and 3.2.3(1)(h) | Equipment Access | Visual | TRUE |  | FALSE
1.1.9 | CT Polarity-Are polarity's oriented the correct direction with reference to the design proposal? | Protocol 10.4.2(1), SMOG Section 3.2.1(1)(b), 3.2.1(1)(c) and 3.2.3(1)(h) | Equipment Access | Visual | TRUE |  | FALSE
ERCOT Point of Interconnection
NUM. | QUESTION | PROTOCOL | RESOURCE TYPE | CHECK METHOD | MEETS REQ. | COMMENT | FOLLOW UP
1.2.1 | Netting Scheme-Does physical distance of 400 yards meet protocol? | Protocol 10.3.2.3 | TDSP Document | Visual | TRUE |  | FALSE
1.2.2 | Are EPS meters connected to the ERCOT grid as shown on the Approved Design Proposal? | Protocol 10.3.2.2 | Approved EPS Design Proposal | Visual | TRUE |  | FALSE
1.2.3 | Are EPS meters compensated once and only once if needed? | Protocol 10.3.2.2 | TDSP Document | TDSP Documentation | TRUE |  | FALSE
Physical Facility Compliance
Facility
NUM. | QUESTION | PROTOCOL | RESOURCE TYPE | CHECK METHOD | MEETS REQ. | COMMENT | FOLLOW UP
2.1.1 | Does facility environment provide acceptable operating conditions for metering equipment? | SMOG Section 1.5.1(1) | Manufacturer Documentation | Visual | TRUE |  | FALSE
2.1.2 | Does facility meet the requirement outlined in the NESC, Article 125a? | SMOG Section 1.5.1(2) | Industry Standard Document | Visual | TRUE |  | FALSE
2.1.3 | Enclosures-Does EPS metering reside in protected enclosure or structure? | SMOG Section 1.5.2(1)(a) | Equipment Access | Visual | TRUE |  | FALSE
2.1.4 | Test Switch Location-Are test switches located at or near the EPS meters? | SMOG Section 1.5.2 | Equipment Access | Visual | TRUE |  | FALSE
2.1.5 | Test Switch Functionality-Are test switches wired to allow for removal of a meter without affecting other EPS meters? | SMOG Section 1.5.2(1)(c) | Equipment Access | Visual | TRUE |  | FALSE
2.1.6 | Test Switch-Is current circuit wired so that during testing there is no disruption to other meters? | SMOG Section 1.5.2(1)(d) | Equipment Access | Visual | TRUE |  | FALSE
2.1.7 | Lighting-Does facility provide adequate lighting? | SMOG Section 1.5.2(1)(b) | Equipment Access | Visual | TRUE |  | FALSE
2.1.8 | Test Output-Is the electrical test output conveniently accessed? | SMOG Section 1.5.2 | Equipment Access | Visual | TRUE |  | FALSE
2.1.9 | Are metering facilitates and secondary devices sealed to protect against unauthorized entry? | Protocol 10.10.1.5 | Equipment Access | Visual | TRUE |  | FALSE
2.1.10 | Are existing seals approved ERCOT seals? | Protocol 10.10.1.5 | Equipment Access | Visual | TRUE |  | FALSE
2.1.11 | Do existing seals match most recent submitted test report? | Protocol 10.10.1.5 | Equipment Access | Visual | TRUE |  | FALSE
Meter Accuracy Test & Load Check Verification
MDAS Form (Channel Information)
NUM. | QUESTION | PROTOCOL | RESOURCE TYPE | CHECK METHOD | MEETS REQ. | COMMENT | FOLLOW UP
3.1.1 | Channel Assignments-Do IDR programmed channels match the submitted MDAS form? | SMOG Section 4.1 | MDAS | TDSP Documentation | TRUE |  | FALSE
3.1.2 | Dials-Do number of energy digits match the submitted MDAS form? | SMOG Section 3.2.2(1)(a) | MDAS | TDSP Documentation | TRUE |  | FALSE
3.1.3 | UOM-Do device Unit of Measure codes match the submitted MDAS form? | SMOG Section 3.2.2(1)(a) | MDAS | TDSP Documentation | TRUE |  | FALSE
3.1.4 | Meter Serial Number, Type & Phone number-Does device serial number, model type and phone number match the submitted MDAS form? | SMOG Section 3.2.2(1)(a) | MDAS | Visual | TRUE |  | FALSE
3.1.5 | Do UOM's, Register ID's & Direction of Flow confirm with MDAS staff? | SMOG Section 3.2.2(1)(a) | MDAS | Visual | TRUE |  | FALSE
Multipliers
NUM. | QUESTION | PROTOCOL | RESOURCE TYPE | CHECK METHOD | MEETS REQ. | COMMENT | FOLLOW UP
3.2.1 | Do pulse constants verify the IDR pulse multiplier values on the MDAS and pulse calculation sheet? | SMOG Section 3.3.2 | TDSP Document | Calculations | TRUE |  | FALSE
3.2.2 | Based on Design Proposal peak load values, does programmed pulse value prevent pulse overflow? | SMOG Section 3.3.2 | TDSP Document | Calculations | TRUE |  | FALSE
3.2.3 | Do present load conditions satisfy the nominal calculated pulse values with reference to the approved design proposal and load calculations? | SMOG Section 4.6 | TDSP Document | Calculations | TRUE |  | FALSE
3.2.4 | Does the IDR generate 25% of maximum pulses for nominal load conditions? | SMOG Section 4.6 | TDSP Document | Calculations | TRUE |  | FALSE
3.2.5 | Do programmed register constants match the Meter Multiplier calculation sheet? | SMOG Section 3.3.1 | TDSP Document | Calculations | TRUE |  | FALSE
3.2.6 | Based on Design Proposal peak load values, does programmed register constant prevent register rollover? | SMOG Section 3.3.1 | TDSP Document | Calculations | TRUE |  | FALSE
3.2.7 | Do register multiplier values agree with calculation formula? | SMOG Section 3.3.1 | TDSP Document | Calculations | TRUE |  | FALSE
Meter Program Parameters
NUM. | QUESTION | PROTOCOL | RESOURCE TYPE | CHECK METHOD | MEETS REQ. | COMMENT | FOLLOW UP
3.3.1 | Are EPS meters internal energy registers mapped to the proper IDR channels? | SMOG Section 4.1 | Meter Program | Visual | TRUE |  | FALSE
3.3.2 | Measured Quantities-Are EPS meters programmed for four quadrant measurement? | SMOG Section 6.3.1 | Meter Program | Visual | TRUE |  | FALSE
3.3.3 | Event Logging-Does EPS meter have all required events enabled? | SMOG Section 6.5.4 | Meter Program | TDSP Documentation | TRUE |  | FALSE
3.3.4 | Diagnostic Checks-Does EPS meter have required diagnostics enabled? | SMOG Section 6.5.1, 6.5.2 | Meter Program | Visual | TRUE |  | FALSE
Calibration Standard
NUM. | QUESTION | PROTOCOL | RESOURCE TYPE | CHECK METHOD | MEETS REQ. | COMMENT | FOLLOW UP
3.4.1 | Test Equipment-Are watthour and varhour standards equal to or better than the accuracy of EPS meters? | SMOG Section 1.6.1 | Manufacturer Documentation | TDSP Documentation | TRUE |  | FALSE
3.4.2 | Standard Certification-Have watthour and varhour standards been tested within the last 120 days? | SMOG Section 1.6.2 | TDSP Document | TDSP Documentation | TRUE |  | FALSE
3.4.3 | Correction Factors-Do correction factors exist for test standards and are they retained with standards? | SMOG Section 1.6.2 | TDSP Document | TDSP Documentation | TRUE |  | FALSE
Testing Records
NUM. | QUESTION | PROTOCOL | RESOURCE TYPE | CHECK METHOD | MEETS REQ. | COMMENT | FOLLOW UP
3.5.1 | Are proper test amps and power factors applied for KWH test? | SMOG Section 1.6.5 | Test Equipment | Visual | TRUE |  | FALSE
3.5.2 | Are KWH functions within allotted accuracy tolerance? | SMOG Section 1.6.5 | TDSP Document | Visual | TRUE |  | FALSE
3.5.3 | Are proper test amps and power factors applied for KVARH test? | SMOG Section 1.6.5 | Test Equipment | Visual | TRUE |  | FALSE
3.5.4 | Are KVARH functions within allotted accuracy tolerance? | SMOG Section 1.6.5 | TDSP Document | Visual | TRUE |  | FALSE
3.5.5 | Test Records- Are test records available for last six years? | SMOG Section 1.7.2(1) | TDSP Document | Visual | TRUE |  | FALSE
3.5.6 | Test Data-Is test data recorded on approved ERCOT Meter Test Report? | SMOG Section 1.8(1)(c) | TDSP Document | Visual | TRUE |  | FALSE
Loss Calculation Verification
Transformer Loss Values
NUM. | QUESTION | PROTOCOL | RESOURCE TYPE | CHECK METHOD | MEETS REQ. | COMMENT | FOLLOW UP
4.1.1 | Does information entered on Loss calculation sheet match the site facility data? | SMOG Section 8 | Equipment Access | Visual | TRUE |  | FALSE
4.1.2 | High Voltage Rating-Does voltage rating match manufacturer sheet? | SMOG Section 8 | Manufacturer Documentation | Visual | TRUE |  | FALSE
4.1.3 | Low Voltage Rating-Does voltage rating match manufacturer sheet? | SMOG Section 8 | Manufacturer Documentation | Visual | TRUE |  | FALSE
4.1.4 | KVA Rating-Does KVA rating match the Loss compensation sheet? | SMOG Section 8 | Manufacturer Documentation | Visual | TRUE |  | FALSE
4.1.5 | Are physical high voltage tap settings being used in loss calculations? | SMOG Section 8 | Equipment Access | Visual | TRUE |  | FALSE
4.1.6 | Are physical low voltage tap settings being used in loss calculations? | SMOG Section 8 | Equipment Access | Visual | TRUE |  | FALSE
4.1.7 | Transformer Connection-Is transformer connected Wye or Delta? | SMOG Section 8 | Equipment Access | Visual | TRUE |  | FALSE
4.1.8 | Transformer Phases-Are there one or three phases? | SMOG Section 8 | Equipment Access | Visual | TRUE |  | FALSE
4.1.9 | Meter Elements-Are correct number of elements used in loss calculation? | SMOG Section 8 | Equipment Access | Visual | TRUE |  | FALSE
4.1.10 | Meter Class-Is correct class rating of meter used in loss calculation? | SMOG Section 8 | Equipment Access | Calculations | TRUE |  | FALSE
4.1.11 | Meter Voltage Rating-Is secondary meter voltage used in loss calculation? | SMOG Section 8 | Equipment Access | Visual | TRUE |  | FALSE
4.1.12 | Percent Impedance-Is nameplate impedance used in loss calculation? | SMOG Section 8 | Equipment Access | Visual | TRUE |  | FALSE
4.1.13 | Percent Excitation-Does excitation match with transformer data sheet? | SMOG Section 8 | Manufacturer Documentation | Visual | TRUE |  | FALSE
4.1.14 | Watt Losses-Does computation of transformer data equal no load watts factor? | SMOG Section 8 | TDSP Document | Calculations | TRUE |  | FALSE
4.1.15 | Var Losses-Does computation of transformer data equal no load var factor? | SMOG Section 8 | TDSP Document | Calculations | TRUE |  | FALSE
4.1.16 | Watt Losses-Does computation of transformer data produce load watt factor? | SMOG Section 8 | TDSP Document | Calculations | TRUE |  | FALSE
4.1.17 | Var Losses-Does computation of transformer data produce load var factor? | SMOG Section 8 | TDSP Document | Calculations | TRUE |  | FALSE
4.1.18 | Is median tap voltage used in loss calculation? | SMOG Section 8 | Equipment Access | Visual | TRUE |  | FALSE
4.1.19 | Auto-Transformer Compensation-Are iron and copper losses included in compensation factors? | SMOG Section 8 | TDSP Document | Visual | TRUE |  | FALSE
Line Losses
NUM. | QUESTION | PROTOCOL | RESOURCE TYPE | CHECK METHOD | MEETS REQ. | COMMENT | FOLLOW UP
4.2.1 | Line Type-What type of line is used in loss calculation? | SMOG Section 8.4 | Industry Standard Document | TDSP Documentation | TRUE |  | FALSE
4.2.2 | Are correct ohms/mile used in loss computations? | SMOG Section 8.4 | Industry Standard Document | TDSP Documentation | TRUE |  | FALSE
4.2.3 | Line Distance-How many miles of line are used in loss calculation? | SMOG Section 8.4 | TDSP Document | Calculations | TRUE |  | FALSE
4.2.4 | Do compensation values and registration values agree with ERCOT approved TLC spreadsheet? | SMOG Section 3.3.3 | TDSP Document | Visual | TRUE |  | FALSE
4.2.5 | Do EPS meters have correct compensation factors (+ or -) programmed in the meters? | SMOG Section 3.3.3 | Meter Program | Visual | TRUE |  | FALSE
Current Transformer Equipment and Circuit Validation
Physical Properties
NUM. | QUESTION | PROTOCOL | RESOURCE TYPE | CHECK METHOD | MEETS REQ. | COMMENT | FOLLOW UP
5.1.1 | BIL Rating-Is CT designed and constructed to ANSI C12.11 or IEEE C57.13-1993 standards? | SMOG Section 7.5.1 | Manufacturer Documentation | Visual | TRUE |  | FALSE
5.1.2 | Winding Configuration-Does CT winding comply with approved typical configurations? | SMOG Section 7.5.3.1 | Manufacturer Documentation | Visual | TRUE |  | FALSE
5.1.3 | Does CT nameplate list the following nameplate items, manufacturer, type of device, serial number, ratios, burden, accuracy class, thermal rating factor, and impulse level? | SMOG Section 7.5.2 | Equipment Access | Visual | TRUE |  | FALSE
5.1.4 | Does nameplate data match submitted Site Certification sheet? | SMOG Section 3.2.3(1)(g) | TDSP Document | Visual | TRUE |  | FALSE
5.1.5 | Does nameplate rated primary current (ratio and RF) match approved EPS Design proposal? | SMOG Section 7.5.3.2 | Approved EPS Design Proposal | Visual | TRUE |  | FALSE
5.1.6 | Rated Secondary Current(wire wound)-Is secondary current rated at 5 amps for rated primary amps? | SMOG Section 7.5.3.3 | Manufacturer Documentation | Visual | TRUE |  | FALSE
5.1.7 | Accuracy Class-Is CT designed for minimum standard accuracy of .3 percent? | SMOG Section 7.5.3.5 | Manufacturer Documentation | Visual | TRUE |  | FALSE
5.1.8 | CT Rating Factors-Does CT possess a standard rating factor of 1.0 or higher at operating temperature? | SMOG Section 7.5.3.7 | Manufacturer Documentation | Visual | TRUE |  | FALSE
5.1.9 | Short Time Thermal Current Rating-Does CT meet the requirements for short time thermal currents as prescribed in IEEE 57.13? | SMOG Section 7.5.3.8 | Manufacturer Documentation | Visual | TRUE |  | FALSE
5.1.10 | Short Time Mechanical Current Rating-Does CT meet the requirements for short time thermal currents as prescribed in IEEE 57.13? | SMOG Section 7.5.3.9 | Manufacturer Documentation | Visual | TRUE |  | FALSE
5.1.11 | Fault Withstand-Does existing CT possess ability to withstand available fault current? | SMOG Section 1.3.1 | TDSP Document | Visual | TRUE |  | FALSE
5.1.12 | Do test switches allow for the measurement of metered quantities and the application of test values? | SMOG Section 1.2.3 | Equipment Access | Visual | TRUE |  | FALSE
CT Quantity
NUM. | QUESTION | PROTOCOL | RESOURCE TYPE | CHECK METHOD | MEETS REQ. | COMMENT | FOLLOW UP
5.2.1 | 4-Wire Wye-Do three CT's exist? | SMOG Section 1.3.2 | Equipment Access | Visual | TRUE |  | FALSE
5.2.2 | 3-Wire Delta-Do two CT's exist? | SMOG Section 1.3.2 | Equipment Access | Visual | TRUE |  | FALSE
Burden
NUM. | QUESTION | PROTOCOL | RESOURCE TYPE | CHECK METHOD | MEETS REQ. | COMMENT | FOLLOW UP
5.3.1 | Is circuit limited to highly accurate billing meters and load control transducers only? | SMOG Section 1.3.4(3) | TDSP Document | Visual | TRUE |  | FALSE
5.3.2 | Are separate isolated secondaries existing between EPS metering and other allowable meter devices? | SMOG Section 1.5.2(1)(c) | TDSP Document | Visual | TRUE |  | FALSE
5.3.3 | Is the total burden on the CT within the CT Burden Rating? | SMOG Section 1.3.3(1) | Equipment Access | Measured Values | TRUE |  | FALSE
5.3.4 | Annual Burden Test-Demonstrated connected burden check? | SMOG Section 1.3.3(2) | Equipment Access | Measured Values | TRUE |  | FALSE
CT Secondary Wiring
NUM. | QUESTION | PROTOCOL | RESOURCE TYPE | CHECK METHOD | MEETS REQ. | COMMENT | FOLLOW UP
5.4.1 | There are no splices in the CT Secondary Wiring? | SMOG Section 1.3.4(1) | Equipment Access | Visual | TRUE |  | FALSE
5.4.2 | Is wire of sound electrical and mechanical integrity? | SMOG Section 1.3.4(2) | Equipment Access | Visual | TRUE |  | FALSE
5.4.3 | Has wire integrity inspection been performed within the last three years? | SMOG Section 1.3.4(2) | TDSP Document | TDSP Documentation | TRUE |  | FALSE
Grounding of CT Circuit
NUM. | QUESTION | PROTOCOL | RESOURCE TYPE | CHECK METHOD | MEETS REQ. | COMMENT | FOLLOW UP
5.5.1 | Return Conductor-Does each set of CT's have one common return conductor? | SMOG Section 1.3.5(1) | Equipment Access | Visual | TRUE |  | FALSE
5.5.2 | Grounding Point-Is there only one grounded point of the common return? | SMOG Section 1.3.5(2) | Equipment Access | Visual | TRUE |  | FALSE
5.5.3 | Ground wire size-Is the ground conductor of the same size as the polarity and common wire? | SMOG Section 1.3.5(4) | Equipment Access | Visual | TRUE |  | FALSE
Induced Voltages
NUM. | QUESTION | PROTOCOL | RESOURCE TYPE | CHECK METHOD | MEETS REQ. | COMMENT | FOLLOW UP
5.6.1 | Cable Routing-Are cables routed so as to minimize induced voltage effects? | SMOG Section 1.3.6(1) | Equipment Access | Visual | TRUE |  | FALSE
5.6.2 | Cable Protection-Is suitable protection available (Meter Handbook 10th Edition Chapter 11 pg 352)? | SMOG Section 1.3.6(2) | TDSP Document | Visual | TRUE |  | FALSE
Paralleling of CT's
NUM. | QUESTION | PROTOCOL | RESOURCE TYPE | CHECK METHOD | MEETS REQ. | COMMENT | FOLLOW UP
5.7.1 | Nominal Rating-Do all CT's have the same ratio? | SMOG Section 1.3.7(1)(a) | Equipment Access | Visual | TRUE |  | FALSE
5.7.2 | Phase Connection-Are paralleled CT's connected to the same phases? | SMOG Section 1.3.7(1)(b) | Equipment Access | Visual | TRUE |  | FALSE
5.7.3 | Secondary connections-Do secondary circuits allow for testing of individual CT's? | SMOG Section 1.3.7(1)(c) | Equipment Access | Visual | TRUE |  | FALSE
5.7.4 | Are CT's paralleled at the meter test switch? | SMOG Section 1.3.7(1)(c) | Equipment Access | Visual | TRUE |  | FALSE
5.7.5 | Grounding Point-Is there only one grounded point for the paralleled CT secondaries? | SMOG Section 1.3.7(1)(d) | Equipment Access | Visual | TRUE |  | FALSE
5.7.6 | Burden Rating-Does each CT possess the ability to support n times the common burden plus its own individual burden within the accuracy class? | SMOG Section 1.3.7(1)(e), and Section 1.3.7(1)(h) | Equipment Access | Visual | TRUE |  | FALSE
5.7.7 | Common Voltage-Do circuits that have paralleled CT's share a common bus that is normally closed? | SMOG Section 1.3.7(1)(f) | Equipment Access | Visual | TRUE |  | FALSE
5.7.8 | Is class rating of meter adequate to measure summation of paralleled currents? | SMOG Section 1.3.7(1)(g) | Equipment Access | Visual | TRUE |  | FALSE
Sizing Current Transformers
NUM. | QUESTION | PROTOCOL | RESOURCE TYPE | CHECK METHOD | MEETS REQ. | COMMENT | FOLLOW UP
5.8.1 | Is CT sized for optimum metering accuracy at peak and minimum loads? | SMOG Section 1.3.8 | MDAS | Calculations | TRUE |  | FALSE
Voltage Transformer Equipment and Circuit Validation
Physical Properties
NUM. | QUESTION | PROTOCOL | RESOURCE TYPE | CHECK METHOD | MEETS REQ. | COMMENT | FOLLOW UP
6.1.1 | Rated Secondary Voltage-Is secondary output of VT rated at 115/69 volts? | SMOG Section 7.5.4.3 | Manufacturer Documentation | Visual | TRUE |  | FALSE
6.1.2 | Accuracy Class-Is VT designed for minimum standard accuracy of .3 percent? | SMOG Section 7.5.4.4 | Manufacturer Documentation | Visual | TRUE |  | FALSE
6.1.3 | Thermal Burden Rating-Does VT meet the IEEE C57.13 requirement for thermal burden? | SMOG Section 7.5.4.5 | Manufacturer Documentation | Visual | TRUE |  | FALSE
VT Quantity
NUM. | QUESTION | PROTOCOL | RESOURCE TYPE | CHECK METHOD | MEETS REQ. | COMMENT | FOLLOW UP
6.2.1 | Are there three, phase to ground voltages for 4-wire wye sites? | SMOG Section 1.4.1(1) | Equipment Access | Measured Values | TRUE |  | FALSE
6.2.2 | Are there three phase to phase voltages for 3-wire delta sites? | SMOG Section 1.4.1(2) and SMOG Section 1.4.1(3) | Equipment Access | Measured Values | TRUE |  | FALSE
6.2.3 | Burden-Is the total VA burden within nameplate rating for each instrument transformer? | SMOG Section 1.4.2 | Equipment Access | Calculations | TRUE |  | FALSE
6.2.4 | Protection-Are fuses of high speed type? | SMOG Section 1.4.3 | Equipment Access | Visual | TRUE |  | FALSE
6.2.5 | Fuses are not installed in the common return or ground circuit? | SMOG Section 1.4.3 | Equipment Access | Visual | TRUE |  | FALSE
VT Secondary Wiring
NUM. | QUESTION | PROTOCOL | RESOURCE TYPE | CHECK METHOD | MEETS REQ. | COMMENT | FOLLOW UP
6.3.1 | Voltage Drop-Is there .3 volt drop or less on secondary? | SMOG Section 1.4.4(1) | Test Equipment | Measured Values | TRUE |  | FALSE
6.3.2 | Wire Integrity-Is wire of sound electrical and mechanical integrity with a documented wire integrity inspection within the last three years and if applicable, has the existence of the high/low impedance ground and existence of the fault monitoring system been verified with the last three years? | SMOG Section 1.4.1(4)(a) and SMOG Section 1.4.4(2) | Equipment Access | Visual | TRUE |  | FALSE
6.3.3 | Have connections of a throw-over relay, if present, been verified to ensure correct voltage phasing is maintained in all operating schemes? | Protocol 10.6.1.1 | TDSP Document | TDSP Documentation | TRUE |  | FALSE
6.3.4 | There are no splices in the VT Secondary Wiring? | SMOG Section 1.4.4(3) | Equipment Access | Visual | TRUE |  | FALSE
6.3.5 | Grounding of VT Circuit-Is there only one ground for the set of secondary windings? | SMOG Section 1.4.5(1) | Equipment Access | Visual | TRUE |  | FALSE
Induced Voltages
NUM. | QUESTION | PROTOCOL | RESOURCE TYPE | CHECK METHOD | MEETS REQ. | COMMENT | FOLLOW UP
6.4.1 | Cable Routing-Are cables routed so as to minimize induced voltage effects? | SMOG Section 1.4.6(1) | Equipment Access | Visual | TRUE |  | FALSE
6.4.2 | Cable Protection-Is suitable protection available to protect against faults and switching generated voltages? | SMOG Section 1.4.6(2) | Equipment Access | Visual | TRUE |  | FALSE
6.4.3 | Loss of Potential-Is secondary being monitored for loss of potential for each phase within the required range and time thresholds? | SMOG Section 6.5.4(1)(k) | Equipment Access | Visual | TRUE |  | FALSE
Three VT-Two CT Metering
Current Transformers
NUM. | QUESTION | PROTOCOL | RESOURCE TYPE | CHECK METHOD | MEETS REQ. | COMMENT | FOLLOW UP
7.1.1 | Are all power transformers primary connections behind the metering point are ungrounded delta, ungrounded wye or phase to phase? | SMOG section 1.3.2 | Equipment Access | Visual | TRUE |  | FALSE
7.1.2 | Has the TDSP verified on an annual basis that all power transformers primary connections behind the metering point are ungrounded delta, ungrounded wye or phase to phase? | SMOG section 1.3.2 | TDSP Document | Visual | TRUE |  | FALSE
7.1.3 | There are no phase-to-ground loads or phase-to-ground sources connected between the metering point and the power transformer primary connections? | SMOG section 1.3.2 | Equipment Access | Visual | TRUE |  | FALSE
7.1.4 | One Line Detail-Does one line detail show all tapped power transformers? | SMOG section 1.3.2 | TDSP Document | Visual | TRUE |  | FALSE
Voltage Transformers
NUM. | QUESTION | PROTOCOL | RESOURCE TYPE | CHECK METHOD | MEETS REQ. | COMMENT | FOLLOW UP
7.2.1 | Are VT's connected delta on secondary? | SMOG Section 1.4.1 | Equipment Access | Visual | TRUE |  | FALSE
7.2.2 | Are there loads connected that provide path for power to ground? | SMOG Section 1.4.1 | Equipment Access | Visual | TRUE |  | FALSE
7.2.3 | Are the VT's connected to the grounding system of the transmission system? | SMOG Section 1.4.1 | Equipment Access | Visual | TRUE |  | FALSE
7.2.4 | Are meter potentials connected phase to common phase? | SMOG Section 1.4.1 | Equipment Access | Visual | TRUE |  | FALSE
7.2.5 | Are secondary of potentials connected the grounding system? | SMOG Section 1.4.1 | Equipment Access | Visual | TRUE |  | FALSE
Energy Storage Resource (ESR) Facility
Energy Storage Resource (ESR)
NUM. | QUESTION | PROTOCOL | RESOURCE TYPE | CHECK METHOD | MEETS REQ. | COMMENT | FOLLOW UP
8.1.1 | Only ESR charging is measured by the EPS meter recording charging energy for the ESR. No other loads or non-allowed devices are connected behind the ESR EPS meter recording charging energy. | Protocols Section 10.2.3(1)(h)&(i), 10.3.2.3 (3) | Equipment Access | Visual
8.1.2 | If the EPS meter recording WSL is not at the Point of Interconnect (POI) it is behind a single POI metering point. | Protocols Section 10.3.2.3 (3)(b) | Equipment Access | Visual
ESR with RE telemetered auxiliary load
NUM. | QUESTION | PROTOCOL | RESOURCE TYPE | CHECK METHOD | MEETS REQ. | COMMENT | FOLLOW UP
8.2.1 | ERCOT has received the Attestation signed by an officer of the Resource Entity. | Protocols Section 10.2.4(2) | RE Document | Visual
8.2.2 | ERCOT has received the independent audit performed by a registered Texas Professional Engineer as part of the Attestation confirming the auxiliary load calculations does not understate the load value. | Protocols Section 10.2.4(2),Protocols Section 10.2.4.1(a)(i) | RE Document | Visual
8.2.3 | The independent audit does include an evaluation the impact of any degradation in accuracy of the sensors over time. | Protocols Section 10.2.4(2) | RE Document | Visual
8.2.4 | The Resource Entity has provided supporting information on the equipment, configuration, drawings and processes used to calculate the telemetry signal, including supporting information on the calculation of the telemetry signal for inclusion in the EPS Design Proposal. | Protocols Section 10.2.4.1(a)(i) | RE Document | Visual
8.2.5 | The Resource Entity Contact information provided is correct and current. | Protocols Section 10.2.4.1(a)(i)(iv) | RE Document | Visual
8.2.6 | EPS meters for ESR with RE telemetered auxiliary load are programmed to record the auxiliary load in channel 5 in accordance with SMOG 4.1 (1). | SMOG 4.1 (1)(c) | Meter Program | Visual
8.2.7 | Calculated auxiliary load is stored in a resource entity device for a minimum of 45 days in 15 minute interval form. | SMOG 5.5(1)(a) | RE Document | Visual
8.2.8 | Calculated auxiliary load is telemetered to both the primary and backup meter. | SMOG 5.5(2) | RE Document | Visual
8.2.9 | Calculated auxiliary load telemetry received by the EPS meters is updated at least every 4 seconds. | SMOG 5.5(3) | RE Document | Visual
8.2.10 | Loss of telemetry - EPS meter is programmed with appropriate alarms to indicate a lost telemetry signal | SMOG 6.5.4(1)(l) | Equipment Access | Visual
8.2.11 | Restoration of telemetry - EPS meter is programmed with appropriate alarms to indicate a restoration of telemetry signal | SMOG 6.5.4(1)(m) | Equipment Access | Visual
Wholesale Storage Load (WSL) with RE telemetered auxiliary load as part of Private Microgrid Island (PMI)
NUM. | QUESTION | PROTOCOL | RESOURCE TYPE | CHECK METHOD | MEETS REQ. | COMMENT | FOLLOW UP
8.3.1 | Generation Resource or ESR that is configured to serve a Customer Load as part of a Private Microgrid Island (PMI), the connection to the Customer Load in the PMI configuration shall be located behind the EPS metering point at the Resource’s POI. | Protocols Section 10.3.2.3 (8) | RE Document | Visual
8.3.2 | The EPS Meter is located to measure the ESR’s gross output net of any internal telemetered auxiliary Load | Protocols Section 10.3.2.3 (8) | RE Document | Visual
8.3.3 | There is a separate TDSP ESI ID (for nodal Settlement) with a Load Serving Entity (LSE) association that was established for the site prior to service of any Load. | Protocols Section 10.3.2.3 (8) | RE Document | Visual

## EPS Meter Standards
Site/Facility: ERCOT EPS Site Audit Date:
Design Proposal Approval Date: Project#: Auditor:
EPS Meter Specifications
Measurement Requirement
NUM. | QUESTION | PROTOCOL | RESOURCE TYPE | CHECK METHOD | MEETS REQ. | COMMENT | FOLLOW UP
1.1.1 | Metered Quantities-Do EPS meters possess the ability to measure true four quadrant measurement? | SMOG Section 6.3.1 | Manufacturer Documentation | Visual | TRUE |  | FALSE
1.1.2 | Kilovars flowing out of ERCOT-Does EPS meter measure var delivered energy in quadrants 1 & 2? | SMOG Section 6.3.1(1)(b) | Meter Program | Visual | TRUE |  | FALSE
1.1.3 | Kilovars flowing into ERCOT-Does EPS meter measure var delivered energy in quadrants 3 & 4? | SMOG Section 6.3.1(1)(c) | Meter Program | Visual | TRUE |  | FALSE
Data Recording Function
NUM. | QUESTION | PROTOCOL | RESOURCE TYPE | CHECK METHOD | MEETS REQ. | COMMENT | FOLLOW UP
1.2.1 | Does recorder provide 4 channel recording capability? | SMOG Section 6.3.3(1)(a) | Manufacturer Documentation | Visual | TRUE |  | FALSE
1.2.2 | Memory-Does EPS meter have sufficient memory to store 45 days of 4 channel 15 minute interval data? | SMOG Section 6.3.3(1)(c) | TDSP Document | Calculations | TRUE |  | FALSE
1.2.3 | Memory Capacity-Does IDR count and store at least of 4,000 counts in a single interval? | SMOG Section 6.3.3(1)(d) | Manufacturer Documentation | Visual | TRUE |  | FALSE
1.2.4 | Recording During Communications-Does the meter record interval data while communications session is active, through any port? | SMOG Section 6.3.3(1)(e) | Equipment Access | Visual | TRUE |  | FALSE
Power Disturbance Functionality
NUM. | QUESTION | PROTOCOL | RESOURCE TYPE | CHECK METHOD | MEETS REQ. | COMMENT | FOLLOW UP
1.3.1 | Retention of Data-During power outage, does meter maintain all data and time/date marks? | SMOG Section 6.3.4(1)(a) | Manufacturer Documentation | Visual | TRUE |  | FALSE
1.3.2 | Does meter resume normal operations upon restoration of power after an outage? | SMOG Section 6.3.4(1)(d) | Manufacturer Documentation | Visual | TRUE |  | FALSE
1.3.3 | Power Outage-Does meter record the time and date of power outage conditions? | SMOG Section 6.3.4(1)(f) | Manufacturer Documentation | Visual | TRUE |  | FALSE
1.3.4 | Does EPS meter have ability to flag intervals when the voltage to the meter power supply is lost for 3 seconds or longer? | SMOG Section 4.4 | Manufacturer Documentation | Visual | TRUE |  | FALSE
Test Mode Functionality
NUM. | QUESTION | PROTOCOL | RESOURCE TYPE | CHECK METHOD | MEETS REQ. | COMMENT | FOLLOW UP
1.4.1 | Normal Mode Suspend-During test mode is recording suspended for IDR and normal registers? | SMOG Section 6.3.5(1)(a) | Manufacturer Documentation | Visual | TRUE |  | FALSE
1.4.2 | Test Mode Security-Is meter programmed to limit unauthorized access to test mode? | SMOG Section 6.3.5(1)(b) | Manufacturer Documentation | Visual | TRUE |  | FALSE
1.4.3 | Test Mode Deactivation-Is meter programmed to exit test mode within one hour or less? | SMOG Section 6.3.5(1)(b) | Manufacturer Documentation | Visual | TRUE |  | FALSE
1.4.4 | Compensated Values-For compensated sites, does meter have the capability to display compensated energy values? | SMOG Section 6.4.1 | Manufacturer Documentation | Visual | TRUE |  | FALSE
1.4.5 | Self Test-Does meter perform self test for register functionality per the SMOG requirements? | SMOG Section 6.5.1 | Manufacturer Documentation | Visual | TRUE |  | FALSE
1.4.6 | Diagnostic Check-In the event of diagnostic failure, does EPS meter store the event that is retrievable by the MDAS? | SMOG Section 6.5.2 | Manufacturer Documentation | Visual | TRUE |  | FALSE
1.4.8 | Event Logging-Is meter programmed to log all events as listed in SMOG? | SMOG Section 6.5.4 | Manufacturer Documentation | Visual | TRUE |  | FALSE
1.4.9 | Local Communications Interface-Does EPS meter possess ability to communicate locally? | SMOG Section 6.6.1 | Manufacturer Documentation | Visual | TRUE |  | FALSE
Accuracy Class
NUM. | QUESTION | PROTOCOL | RESOURCE TYPE | CHECK METHOD | MEETS REQ. | COMMENT | FOLLOW UP
1.5.1 | Are EPS meters designed to meet ANSI C12.20, 0.2 accuracy class? | SMOG Section 6.7.1 | Manufacturer Documentation | Visual | TRUE |  | FALSE
1.5.2 | Start-up Delay-Does meter begin calculations within 15 seconds of power application to the metering electronics. | SMOG Section 6.7.3 | Manufacturer Documentation | Visual | TRUE |  | FALSE
Meter Conformance Requirements
TDSP Approved Meters
NUM. | QUESTION | PROTOCOL | RESOURCE TYPE | CHECK METHOD | MEETS REQ. | COMMENT | FOLLOW UP
2.1.1 | Firmware-Does documentation exist showing the current and pervious versions of firmware along with the dates of deployment, discontinuation, and reasons for discontinuations? | SMOG Section 6.12.2(2)(a)(i) | TDSP Document | Visual | TRUE |  | FALSE
2.1.2 | Software-Does documentation exist showing the current and pervious versions of software along with the dates of deployment, discontinuation, and reasons for discontinuations? | SMOG Section 6.12.2(2)(a)(ii) | TDSP Document | Visual | TRUE |  | FALSE
2.1.3 | Certification Letter-Does TDSP possess letter certifying compliance of meter with ANSI/IEC standards and ERCOT Protocols and SMOG? | SMOG Section 6.12.2(2)(b) | Manufacturer Documentation | Visual | TRUE |  | FALSE
2.1.4 | Test Data-Does TDSP possess document from manufacturer detailing testing certification? | SMOG Section 6.12.2(2)(c) - 6.12.2(2)(c)(g) | Manufacturer Documentation | Visual | TRUE |  | FALSE
2.1.5 | Drawings/Technical Manuals-Does TDSP possess necessary schematics and technical manuals for installation and maintenance of device? | SMOG Section 6.12.2(2)(c) - 6.12.2(2)(c)(g) | Manufacturer Documentation | Visual | TRUE |  | FALSE