## Introduction
TLF = Transmission Loss Factor
SIEL = Settlement Interval ERCOT system Load
SSC = Seasonal Slope Coefficient = (SONLF - SOFFLF)/(SONL - SOFFL)
SIC = Seasonal Intercept Coefficient = [(SOFFLF * SONL) - (SONLF * SOFFL)]/(SONL - SOFFL)
SONLF = Seasonal on-peak percent loss factor
SOFFLF = Seasonal off-peak percent loss factor
SONL = Seasonal on-peak Load value
SOFFL = Seasonal off-peak Load value

## 2020_Transmission_Losses
TRANSMISSION LOSS FACTORS for 2020 as of 11/08/19
Data from Seasonal SSWG Base Cases Updated with updates received by 11/08/19
Transmission Loss is from 60 kV or higher reporting only
NOIE INTERNAL refers to generation, load and losses behind NOIE meters
|  | ERCOT TOTAL |  |  |  | AEN (9) NOIE INTERNAL TOTAL |  |  |  |  | CPS (5) NOIE INTERNAL TOTAL |  |  |  |  | COG (20) NOIE INTERNAL TOTAL |  |  |  |  | GEUS (21) NOIE INTERNAL TOTAL |  |  |  |  | COD (19) NOIE INTERNAL TOTAL |  |  |  |  | BPUB (15) NOIE INTERNAL TOTAL |  |  |  |  | BTU (22) NOIE INTERNAL TOTAL |  |  |  |  | COCS (23) NOIE INTERNAL TOTAL
Case Type | Base Case Name | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV | Total Base Case Loss MW | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen)
Spring On Peak | 2020_SPG1 | 77783.7 | 76147.7 | 1484.82 | 1608.76 | 1586.5 | 2566.5 | 34.26 | 36.7 | 1016.7 | 3709.9 | 4314.4 | 26.19 | 31.1 | 635.6 | 480.9 | 424 | 3.31 | 5.1 | -51.8 | 24 | 64.5 | 0.11 | 0.2 | 40.7 | 192.1 | 349.9 | 1.43 | 1.9 | 159.7 | 94 | 300 | 0.73 | 1 | 207 | 209.7 | 315.8 | 2.98 | 3.5 | 109.6 | 0 | 164.3 | 0.17 | 0.2 | 164.5
Spring Off Peak | 2020_SPG2 | 50752.2 | 49490.7 | 1160.97 | 1236.46 | 1410.4 | 1544.5 | 17.26 | 18.9 | 153 | 2271.3 | 2215.4 | 11.92 | 14.2 | -41.7 | 106.8 | 199 | 0.67 | 0.7 | 92.9 | 0 | 40.2 | 0.03 | 0 | 40.2 | 47.1 | 240.1 | 0.57 | 0.7 | 193.7 | 39.2 | 158.5 | 0.25 | 0.5 | 119.8 | 12.6 | 158.9 | 1.17 | 1.2 | 147.5 | 0 | 80.3 | 0.06 | 0.1 | 80.4
Summer On Peak | 2020_SUM1 | 90277.8 | 88193.7 | 1850.66 | 1998.68 | 1937.4 | 2904.5 | 49.21 | 51.7 | 1018.8 | 5031.3 | 5352 | 39.53 | 46.9 | 367.6 | 816.8 | 589 | 5.39 | 8.1 | -219.7 | 105.5 | 116.1 | 0.54 | 1 | 11.6 | 222.5 | 405.7 | 2.22 | 2.8 | 186 | 104 | 322.3 | 0.71 | 1 | 219.3 | 256 | 392 | 4.3 | 5.1 | 141.1 | 0 | 212.3 | 0.25 | 0.2 | 212.5
Summer Off Peak | 2020_SUM2 | 58365 | 57090.8 | 1171.39 | 1249.4 | 1236 | 1666.5 | 15.65 | 16.8 | 447.3 | 3340.8 | 2957 | 25.17 | 29.7 | -354.1 | 113.7 | 212 | 1.04 | 1 | 99.3 | 0 | 68.6 | 0.09 | 0.1 | 68.7 | 181.1 | 206.9 | 0.81 | 1.2 | 27 | 46 | 147.8 | 0.17 | 0.4 | 102.2 | 141.1 | 203.4 | 1.23 | 1.5 | 63.8 | 0 | 106.8 | 0.06 | 0.1 | 106.9
Fall On Peak | 2020_FAL1 | 75672.6 | 73981.3 | 1569.75 | 1682.02 | 1381.1 | 2457 | 36.85 | 38.9 | 1114.8 | 2635.6 | 4405 | 22.26 | 26.3 | 1795.7 | 468.4 | 384 | 2.7 | 4.4 | -80 | 24 | 86.7 | 0.18 | 0.3 | 63 | 65.3 | 314.2 | 0.99 | 1.1 | 250 | 104 | 292.5 | 0.65 | 1 | 189.5 | 80.1 | 370 | 3.36 | 3.4 | 293.3 | 0 | 164.3 | 0.32 | 0.3 | 164.6
Fall Off Peak | 2020_FAL2 | 49797.5 | 48677.9 | 1039.4 | 1111.8 | 976.9 | 1490.5 | 11.06 | 11.8 | 525.4 | 1048.5 | 2655 | 10.71 | 11.5 | 1618 | 107.1 | 195 | 0.55 | 0.6 | 88.5 | 0 | 51.5 | 0.05 | 0 | 51.5 | 0 | 131.9 | 0.38 | 0.4 | 132.3 | 42 | 150.3 | 0.23 | 0.4 | 108.7 | 20 | 188.2 | 1.12 | 1.1 | 169.3 | 0 | 81.9 | 0.08 | 0.1 | 82
Winter On Peak | 2021_WIN1 | 82788.8 | 81081.5 | 1553.47 | 1692.04 | 1360.1 | 2190.3 | 43.33 | 45.3 | 875.5 | 4561.2 | 4355 | 36.28 | 42.9 | -163.3 | 325.9 | 481 | 3.09 | 3.2 | 158.3 | 16 | 97.8 | 0.21 | 0.2 | 82 | 212.2 | 273.8 | 1.55 | 2.2 | 63.8 | 68 | 295 | 0.79 | 1 | 228 | 254.9 | 397.9 | 4.02 | 4.8 | 147.8 | 0 | 141 | 0.2 | 0.2 | 141.2
Winter Off Peak | 2021_WIN2 | 60665.3 | 59332.9 | 1231.82 | 1316.2 | 1266.7 | 1781.3 | 22.56 | 24.3 | 538.9 | 3696 | 2928 | 25.1 | 29.8 | -738.2 | 126.2 | 234 | 1.09 | 1.1 | 108.9 | 0 | 73.6 | 0.1 | 0.1 | 73.7 | 99.4 | 139.7 | 0.68 | 0.9 | 41.2 | 28 | 187.7 | 0.34 | 0.5 | 160.2 | 113.7 | 272.9 | 1.53 | 1.7 | 160.9 | 0 | 102.4 | 0.11 | 0.1 | 102.5
Self Serve Load Modeled in Base Cases that does not contribute to transmission losses. | [8 empty] | NOIE TOTALS
Case Type | Base Case Name | CNP Self Serve MW | AEP Self Serve MW | TNMP Self Serve MW | BTU Self Serve MW | ONCOR Self Serve MW | AEP DC Ties Model MW | TOTAL |  | NOIE LOAD MW | NOIE External Resources MW | NOIE Load Served from Internal Resources MW | NOIE TOTAL Loss Above 60 kV | Base Case Name
Spring On Peak | 2020_SPG1 | 2669 | 1482.68 | 610 | 42.96 | 169.57 | 0 | 4974.21 |  | 8499.4 | 2282 | 6217.4 | 69.18 | 2020_SPG1
Spring Off Peak | 2020_SPG2 | 2669 | 1425.81 | 560 | 0 | 165.22 | 0 | 4820.03 |  | 4636.9 | 785.8 | 3851.1 | 31.93 | 2020_SPG2
Summer On Peak | 2020_SUM1 | 2669 | 1507.83 | 610 | 43 | 206.39 | 0 | 5036.22 |  | 10293.9 | 1937.2 | 8356.7 | 102.15 | 2020_SUM1
Summer Off Peak | 2020_SUM2 | 2669 | 1434.15 | 518.5 | 10.19 | 206.59 | 0 | 4838.43 |  | 5569 | 561.1 | 5007.9 | 44.22 | 2020_SUM2
Fall On Peak | 2020_FAL1 | 2669 | 1420.31 | 610 | 23.26 | 206.36 | 0 | 4928.93 |  | 8473.7 | 3790.9 | 4682.8 | 67.31 | 2020_FAL1
Fall Off Peak | 2020_FAL2 | 2669 | 1389.17 | 527.4 | 0 | 202.56 | 0 | 4788.13 |  | 4944.3 | 2775.7 | 2168.6 | 24.18 | 2020_FAL2
Winter On Peak | 2021_WIN1 | 2669 | 1452.12 | 610 | 33.76 | 152.28 | 0 | 4917.16 |  | 8231.8 | 1533.3 | 6698.5 | 89.47 | 2021_WIN1
Winter Off Peak | 2021_WIN2 | 2669 | 1428.17 | 536 | 0 | 149.65 | 0 | 4782.82 |  | 5719.6 | 448.1 | 5271.5 | 51.51 | 2021_WIN2
SEASON | ERCOT WITH SELF SERVE LOAD CORRECTIONS |  |  |  |  | AEN NOIE INTERNAL |  |  |  |  | CPS NOIE INTERNAL |  |  |  |  | COG NOIE INTERNAL |  |  |  |  | GEUS NOIE INTERNAL |  |  |  |  | COD NOIE INTERNAL |  |  |  |  | BPUB NOIE INTERNAL |  |  |  |  | BTU NOIE INTERNAL |  |  |  |  | COCS NOIE INTERNAL
| SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF
SPRING | 72809.49 | 45932.17 | 2.039% | 2.528% |  | 2566.5 | 1544.5 | 1.317% | 1.105% |  | 4314.4 | 2215.4 | 0.6034% | 0.5352% |  | 424 | 199 | 0.7746% | 0.3356% |  | 64.5 | 40.2 | 0.1703% | 0.07457% |  | 349.9 | 240.1 | 0.407% | 0.2368% |  | 300 | 158.5 | 0.2427% | 0.1575% |  | 315.8 | 158.9 | 0.9348% | 0.7309% |  | 164.3 | 80.3 | 0.1034% | 0.07466%
SUMMER | 85241.58 | 53526.57 | 2.171% | 2.188% |  | 2904.5 | 1666.5 | 1.666% | 0.9304% |  | 5352 | 2957 | 0.7332% | 0.844% |  | 589 | 212 | 0.9068% | 0.4882% |  | 116.1 | 68.6 | 0.463% | 0.131% |  | 405.7 | 206.9 | 0.5442% | 0.39% |  | 322.3 | 147.8 | 0.2198% | 0.1149% |  | 392 | 203.4 | 1.085% | 0.6011% |  | 212.3 | 106.8 | 0.1176% | 0.05615%
FALL | 70743.67 | 45009.37 | 2.219% | 2.309% |  | 2457 | 1490.5 | 1.478% | 0.7366% |  | 4405 | 2655 | 0.5028% | 0.4018% |  | 384 | 195 | 0.6982% | 0.2813% |  | 86.7 | 51.5 | 0.2072% | 0.09699% |  | 314.2 | 131.9 | 0.3141% | 0.2873% |  | 292.5 | 150.3 | 0.2217% | 0.1528% |  | 370 | 188.2 | 0.8999% | 0.5916% |  | 164.3 | 81.9 | 0.1944% | 0.09758%
WINTER | 77871.64 | 55882.48 | 1.995% | 2.204% |  | 2190.3 | 1781.3 | 1.94% | 1.251% |  | 4355 | 2928 | 0.8262% | 0.85% |  | 481 | 234 | 0.6383% | 0.4637% |  | 97.8 | 73.6 | 0.2143% | 0.1357% |  | 273.8 | 139.7 | 0.5629% | 0.4844% |  | 295 | 187.7 | 0.2671% | 0.1808% |  | 397.9 | 272.9 | 1% | 0.5575% |  | 141 | 102.4 | 0.1416% | 0.1073%
TRANSMISSION LOSS FACTORS FOR INSTALLATION IN ERCOT SYSTEMS IN RED BOXES
SEASON | ERCOT WITH SELF SERVE, MODEL & NOIE INTERNAL LOAD CORRECTIONS |  |  |  |  | AEN NOIE INTERNAL |  |  |  |  | CPS NOIE INTERNAL |  |  |  |  | COG NOIE INTERNAL |  |  |  |  | GEUS NOIE INTERNAL |  |  |  |  | COD NOIE INTERNAL |  |  |  |  | BPUB NOIE INTERNAL |  |  |  |  | BTU NOIE INTERNAL |  |  |  |  | COCS NOIE INTERNAL
| SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC
SPRING | -1.8166e-05 | 3.362 |  |  |  | 0.00020758 | 0.78456 |  |  |  | 3.2493e-05 | 0.46319 |  |  |  | 0.0019514 | -0.05277 |  |  |  | 0.0039375 | -0.083716 |  |  |  | 0.00155 | -0.13531 |  |  |  | 0.00060256 | 0.061974 |  |  |  | 0.0012995 | 0.52445 |  |  |  | 0.00034165 | 0.04723
SUMMER | -5.4708e-07 | 2.2177 |  |  |  | 0.00059425 | -0.059963 |  |  |  | -4.6275e-05 | 0.98085 |  |  |  | 0.0011105 | 0.25276 |  |  |  | 0.0069882 | -0.34837 |  |  |  | 0.00077594 | 0.22942 |  |  |  | 0.00060126 | 0.026022 |  |  |  | 0.002566 | 0.079156 |  |  |  | 0.00058266 | -0.0060804
FALL | -3.5117e-06 | 2.4674 |  |  |  | 0.00076675 | -0.40628 |  |  |  | 5.7729e-05 | 0.2485 |  |  |  | 0.0022061 | -0.14894 |  |  |  | 0.0031304 | -0.064221 |  |  |  | 0.00014716 | 0.26786 |  |  |  | 0.00048478 | 0.079931 |  |  |  | 0.0016961 | 0.27239 |  |  |  | 0.0011748 | 0.0013699
WINTER | -9.5226e-06 | 2.7364 |  |  |  | 0.0016852 | -1.7512 |  |  |  | -1.6658e-05 | 0.89873 |  |  |  | 0.00070712 | 0.29819 |  |  |  | 0.0032471 | -0.1033 |  |  |  | 0.00058554 | 0.4026 |  |  |  | 0.000804 | 0.029903 |  |  |  | 0.0035414 | -0.40894 |  |  |  | 0.00088955 | 0.016217
EFFECTIVE DATES | SEASON
03/01/2020 - 05/31/2020 | SPRING
06/01/2020 - 09/30/2020 | SUMMER
10/01/2020 - 11/30/2020 | FALL
12/01/2021 - 02/28/2021 | WINTER