## Slide 1
Proposal for DC-Coupled Resources (KTC-11)
Sai Moorty
Principal, Market Design and Analysis
BESTFORCE Meeting
January 17, 2020

## Slide 2: Acronym
KTC – Key Topic and Concept related to BESTF
ESS – Energy Storage Systems
POI – Point of Interconnection
RARF – Resource Asset Registration Form
RIOO – Resource Integration and Ongoing Operations
PVG – Photo-Voltaic Generation
PVGR – Photo-Voltaic Generation Resource
WGR – Wind Generation Resource
WG – Wind Generation
PVGR – Photo-Voltaic Generation Resource
MPC – Max Power Consumption
LPC – Low Power Consumption
LRL – Low Reasonability Limit
HRL – High Reasonability Limit
LPC – Low Power Consumption

## Slide 3: Key Topics & Concepts
This presentation is specific to DC-Coupled Resources (KTC-11) and does not address AC-Coupled Resources (KTC-12)
Contents:
  Draft Definition
  KTC-11.1 Registration
  KTC-11.2 Participation Model (EMS and MMS)
  KTC-11.3 Forecasting
  KTC-11.4 Should existing performance exemptions to IRR apply?
  KTC-11.5 Mitigation treatment in SCED
  KTC-11.6 WSL Treatment
  KTC-11.7 Data Requirements from QSEs
  KTC-11.8 Interconnection Issues

## Slide 4: Draft Definition
DC-Coupled Resource
One or more Energy Storage Systems (ESS) combined with one or more wind and/or solar generators behind a single point of interconnection (POI), where these combined technologies are interconnected within the site using direct current (DC) equipment. The combined technologies are then connected to the ERCOT grid using the same direct current-to-alternating current (DC-to-AC) inverter(s).

## Slide 5: KTC-11.1 Registration
Because an Energy Storage System (ESS) within a DC-Coupled Resource will at times charge from the grid, the DC-Coupled Resource should register as an Energy Storage Resource (ESR) with a DC-Coupled attribute so that ERCOT systems can differentiate it from a stand-alone Energy Storage Resource (ESR)
RARF/RIOO: The same level of detail for the generation (i.e., solar or wind) portion of the DC-Coupled Resource will be provided in the Resource registration data (e.g., details of collector system/wind turbines, etc.)
Out of scope: Further discussion will be needed if a proposed DC-Coupled Resource does not include an Energy Storage System

## Slide 6: Example: DC-Coupled Resource (Solar + Battery)
DC-DC Converter
-
-
meter
BKR-1
BKR-2
BKR-3
BKR-4
Rest of Grid
+
-
-
+
Battery
Power Electronics
-
~
Solar and battery are coupled on the DC side
Inverter Rating
+- 100 MW (MVA)
ESS (Battery) Rating
+- 20 MW
PVG Rating
+ 100 MW
BKR-5

## Slide 7: ERCOT Evolution for Energy Storage Resources
Registration
(RARF or RIOO)
Siebel, NMMS, EMS, MMS, Settlements
Phase
A
GR
GR
CLR
CLR
Today
C
Single
Resource
Single
Resource
EMS Upgrade + RTC Go-Live 2024
Mark the GR and CLR so that it can be seen they are a pair
ESR
ESR
ESR
ESR
B
By Dec 31, 2020
Single
Resource
GR
ESR
CLR
ESR
‘Combo Model Era’
‘Single Model Era’

## Slide 8
DC-Coupled Resources in the ‘Combo Model’ ESR Era
(Prior to Single Model ESR implementation)

## Slide 9: DC-Coupled ESR in the Combo Model Era
ESS-Charge
MPC (max) = 20 MW
LPC (min) = 0 MW
PVG + ESS-Discharge
HRL = 100 MW
LRL = 0 MW
HSL <= 100 MW
LSL >= 0 MW
meter
BKR-1
BKR-2
BKR-3
BKR-4
Rest of Grid
BKR-5

## Slide 10: Combo Model DC-Coupled ESR Requirements
Treated within ERCOT systems as an ESR (GR/CLR combo)
Separate telemetry will be required from all generators and ESSs within a DC-Coupled Resource (details in following slides)
PVG/WGR forecasted MW will be limited to the inverter rating
Mitigated Offer Cap: Same as Battery ESR or PVGR? Needs more discussion
GREDP and Base Point Deviations:
  Option 1: Same rules as a thermal Generating Resource -- i.e., not afforded the exception given to IRRs;
  or
  Option 2: A DC-Coupled Resource will be required to follow ERCOT Dispatch Instructions at all times similar to thermal units when the DC-Coupled Resource is carrying an Ancillary Service responsibility and its net injection/ withdrawal into/from ERCOT grid includes non-zero telemetered MW from the ESS(s). During all other SCED/Settlement intervals, a DC-Coupled Resource could be treated like a WGR and PVGR when calculating their BP Deviation and GREDP performance metrics.

## Slide 11: Combo Model DC-Coupled ESR Requirements
Generator(s) within a DC-Coupled Resource (e.g., PVG/WG + ESS-Discharge) will provide the following information:
  Three-Part Energy Offer
  COP (HSL cannot exceed the Inverter rating)
    ERCOT will populate the COP HSL with the generators’ forecasted output. QSEs will have the ability to modify (lower or raise) the COP HSL; for example, raise the HSL if the ESS is capable of and the QSE intends to inject additional MW without violating inverter rating)
    COP HSL values will be used for RUC capacity short calculations
  Outage/Deration
  Telemetry
    The usual telemetry required of stand-alone GRs: Net/Gross MW, Resource Status, Breaker Status, AVR Status, Ramp Rate, HSL, LSL, AS Responsibilities, Regulation Participation Factors, etc.
    Telemetry required for forecasting the solar or wind portion of a DC-Coupled Resource will be the same as for a stand-alone WGR or PVGR
    The ESS(s) within a DC-Coupled Resource will provide the same State of Charge-related telemetry required of a stand-alone ESR

## Slide 12: Combo Model DC-Coupled ESR Requirements
ESS-Charge (Load side of the battery) will provide the following:
  RTM Energy Bid
  COP
    MPC cannot exceed the inverter rating
    COP reflects the QSE’s intention to charge the ESS portion of the DC-Coupled Resource
  Outage/Deration
  Telemetry
    The usual telemetry required of all ESR-CLRs: Net Load MW, Resource Status, Breaker Status, Ramp Rate, MPC, LPC, AS Responsibilities, Regulation Participation Factors, etc.

## Slide 13: Combo Model DC-Coupled ESR Requirements
PRC and ORDC Online Reserve calculation will be calculated consistent with droop and dead-band settings limited by energy injection that can be sustained for a minimum of 15 minutes, similar to that for a stand-alone ESR. The calculation will take into account the capability of both ESS and PVGR/WGR.
Real-Time and Next Day Studies will use COPs
Operational Planning Horizon Studies will use the expected operational behavior of an IRR to build these singular time point study cases
Outage Coordination Studies will use the expected operational behavior of an IRR consistent with current practice
Planning studies – details to be worked out

## Slide 14
DC-Coupled Resources in the ‘Single Model’ ESR Era
(Single Model to be implemented simultaneously with RTC go-live, 2024)

## Slide 15: Example: Single Model ESR
ESR modeling construct
HRL = 100 MW
LRL = - 20 MW
HSL <= 100 MW
LSL >= - 20 MW
BKR-5
meter
BKR-1
BKR-2
BKR-3
BKR-4
Rest of Grid

## Slide 16: Single Model DC-Coupled ESR Requirements
For a DC-Coupled Resource, both the generation side – generator(s) plus the discharging side of the ESS (e.g., PV+ESS-Discharge) – and the Load side of the ESS (ESS-Charge) will provide the following information:
  Energy Offer/Bid Curve
  COP (HSL cannot exceed the Inverter rating, LSL can be negative)
    ERCOT will populate the COP HSL with the generators’ forecasted output. QSEs will have the ability to modify (lower or raise) the COP HSL; for example, raise the HSL if the ESS is capable of and the QSE intends to inject additional MW without violating the inverter rating)
    COP LSL reflects the QSE’s intention to charge the energy storage part of DC Coupled Resource.
  Outage/Deration
  Telemetry
    The usual telemetry required of all ESRs in the single model/RTC era: Net/Gross MW, Resource Status, Breaker Status, AVR Status, Ramp Rate, HSL, LSL,, etc.
    Telemetry required for forecasting the solar or wind portion of a DC-Coupled Resource will be the same as for a stand-alone WGR or PVGR
    The ESS(s) within a DC-Coupled Resource will provide the same State of Charge-related telemetry required of a stand-alone ESR

## Slide 17: Single Model DC-Coupled ESR Requirements
Many provisions will carry over from the combo model era, including:
PVG/WG forecasting
Mitigated Offer Cap
GREDP and Base Point Deviations
PRC calculations
Real-Time and Next Day Studies
Operational Planning Horizon Studies
Outage Coordination Studies will use the expected operational behavior of an IRR consistent with current practice
Planning studies

## Slide 18: KTC-11.6 WSL Treatment of DC-Coupled Resource
EPS Metering is required for Wholesale Storage Load (WSL) treatment
  WSL must be separately metered from all other Facilities
EPS Metering equipment must be certified to ANSI Standards
  There is no ANSI Standard for DC metering
  ANSI C12 SC32 DC Metering Working Group has been formed to address DC meter, DC voltage sensor and DC current sensor performance criteria
WSL treatment for the ESS portion of a DC-Coupled Resource is dependent upon ANSI certified DC Metering

## Slide 19: KTC-11.8 Interconnection Issues
Interconnecting Entity (IE) wants to add new energy storage to an existing PV or ESR behind the same inverter.
  Inverter rating will ensure the maximum this facility can generate into ERCOT grid will not change
  Under today’s rules, GINR process requires new registration and studies for this added capacity
  Reactive requirements for this facility would be based on total capacity of the PV and ESS behind the inverter
We think a new streamlined GINR Process is needed
  Some of the studies that are required under today’s process would not provide any additional insight because new energy storage capacity is connecting using the same existing inverter

## Slide 20: KTC-11.8 Interconnection Issues
Interconnecting Entity (IE) wants to add new DC-Coupled Resource into ERCOT, by installing 250 MW of PV and 200 MW of Storage connected to ERCOT grid using shared inverters with the total rating of 250 MW
  Inverter rating will ensure 250 MW will be the maximum this facility can generate into ERCOT grid
  Under today’s rules, GINR process requires registration and studies for this facility at 450 MW Pmax
  Today the reactive requirements for this facility would be based on 450 MW Pmax
We think IE should be able to register this facility at 250 MW Pmax and the GINR studies should be conducted at 250 MW
Under KTC-13, the BESTF will take up discussions regarding co-locating an AC connected ESS at an existing generation site without increasing previously studied and approved POI Pmax.
  New AC connected self limiting Resources will also be discussed under KTC-13.

## Slide 21
Discussion