## Slide 1
ERCOT Frequency Control Report
December 2019
ERCOT
Operations Planning
PDCWG | January 14th, 2020

## Slide 2: Summary of December 2019
CPS1: 178.28%
Current CPS1 12-Month Rolling Average: 174.80%
0 BAAL Exceedance
0 hourly CPS1 score below 100%
BAAL-003 Events have updated through 2018
2018 BAAL-003 FRM Performance: -843.17
2019 RMS1 Statistics
  Mean: 13.96 mHz
  Min: 12.1 mHz
  Max: 15.96 mHz
Energy Statistics
  Total Energy: 29,226,166 MWh
  Wind Energy: 6,609,062 MWh
  Percent Energy from Wind: 22.61%
  Solar Energy: 311,813 MWh
  Percent Energy from Solar: 1.04%
Minimum System Inertia
  Mean: 188,904
  Max: 243,903 on Dec 18th
  Min: 154,996 on Dec 6th
Notes: Mean: 188,904
Max: 243,903 on Dec 18th
Min: 154,996 on Dec 6th

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
Dec-19 CPS1 (%): 178.28
Notes: Outliers:
12/10/2019 06:00 108.4%
Generation deviation due to steep up ramp rate from wind

## Slide 5: BAAL Exceedances & Violations
There was 0 BAAL exceedances in Dec

## Slide 6: 15-Minute Average CPS1%
Dec-19 CPS1 (%): 178.28

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 174.80%

## Slide 8: Daily RMS1 of ERCOT Frequency by Year
Notes:   Mean: 15.00 mHz

## Slide 9: Daily RMS1 of ERCOT Frequency by Month

## Slide 10: Daily RMS1 of ERCOT Frequency by Month
Notes: Mean: 13.96 mHz
Min: 12.1 mHz
Max: 15.96 mHz

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison

## Slide 13: Frequency Profile Comparison

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2018 BAL-003 Selected Events – Update
Notes: BAL-003

## Slide 19: Op. Year 2018 BAL-003 FRM Performance - Update

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 29,226,166 MWh

## Slide 22: Total Energy from Wind Generation
Notes: 6,609,062 MWh

## Slide 23: % Energy from Wind Generation
Notes: 22.61%

## Slide 24: Total Energy From Solar Generation
Notes: 311,813 MWh

## Slide 25: % Energy from Solar Generation
Notes: 1.07%

## Slide 26: ERCOT Energy Statistics for the Decade

## Slide 27: Total Energy

## Slide 28: Total Energy from Wind Generation

## Slide 29: % Energy from Wind Generation

## Slide 30: Total Energy From Solar Generation

## Slide 31: % Energy from Solar Generation
Notes: Larger Total Energy for 2019 compared to 2018

## Slide 32: ERCOT System Inertia

## Slide 33: Daily Minimum System Inertia
Notes: Minimum Inertia = 154,997 MW*s on 12/06/2019
Previous Minimum was 128,759 MW*s on 11/18/2018.
Data:
Mean: 188,904
Max: 243,903 on Dec 18th
Min: 154,996 on Dec 6th

## Slide 34: Questions?
Thank you!